Helios EPC Solutions Pvt. Ltd.

CIN: U40300GJ2009PTC057890

BID RESPONSE
for
Tender Ref. GSPCL/SOLAR/2026/EPC-014
Design, Supply, Installation, Testing & Commissioning of 5 MW Grid-Connected Solar PV Power Plant with 5-Year O&M

| Field | Details |
| --- | --- |
| Bidder Reference | RESPONSE_DOC_S3 |
| Company Name | Helios EPC Solutions Pvt. Ltd. |
| Date of Submission | 10-Mar-2026 |
| Overall Status (as of Evaluation) | TECHNICALLY QUALIFIED - Financial Bid Opened - Deviation Under Committee Review |

# 1. Cover Letter & Understanding of Scope

Helios EPC Solutions Pvt. Ltd. confirms having read and understood the complete Scope of Work, Technical Requirements, Commercial Requirements, and Terms & Conditions set out in the Tender Document GSPCL/SOLAR/2026/EPC-014, and hereby submits its offer for the Design, Supply, Installation, Testing & Commissioning of the 5 MW Grid-Connected Solar PV Power Plant at Village Bhachau, Kutch District, along with 5-Year Comprehensive O&M, on the terms set out herein.

# 2. Eligibility Compliance Statement

| Criteria | Bidder Submission |
| --- | --- |
| EC-1: Average Annual Turnover (last 3 FY) | ₹28.6 Cr / ₹31.2 Cr / ₹30.5 Cr ¦ Average: ₹30.10 Cr |
| EC-2: Relevant Experience | 5 completed solar EPC projects including 5.5 MW (Jamnagar, 2023) and 6 MW (Banaskantha, 2024); strongest project portfolio among bidders. |
| EC-4: Quality Certifications (ISO) | ISO 9001:2015, ISO 14001:2015, ISO 45001:2018 - all valid, all submitted |
| EC-7: EMD | ₹75,00,000 Bank Guarantee, ICICI Bank, valid 180 days - CONFORMS |
| Overall Eligibility Determination | COMPLIANT - all criteria met |

# 3. Technical Evaluation Summary

Technical Score Awarded by Evaluation Committee: 88 / 100 (Qualifying threshold: 60/100)

Highest technical score - excellent design documentation, superior experience portfolio, robust execution schedule.

# 4. Deviations from Tender Requirements

| Clause / Requirement | Deviation Stated | Evaluation Committee Assessment |
| --- | --- | --- |
| Inverter Efficiency (TR-3) | Proposed central inverter efficiency 97.5% against required minimum 98.0% | Moderate - under review; Evaluation Committee to assess energy yield impact before waiver decision |

# 5. Clarifications Sought & Bidder Responses

| Ref. | Clarification Sought by GSPCL | Bidder Response |
| --- | --- | --- |
| CL-1 | Justify inverter efficiency shortfall and its impact on guaranteed Performance Ratio | Bidder submitted PVsyst simulation claiming PR of 80.3% is still achievable; under technical review |
| CL-2 | Confirm willingness to revise price following negotiation invitation | Confirmed; revised price schedule submitted |

# 6. Stage-wise Bid Value

## Stage 1 - Initial Financial Bid (as submitted on 10-Mar-2026)

Total Base Price: ₹19,40,00,000   |   GST @ 13.8%: ₹2,67,72,000   |   Total Bid Value: ₹22,07,72,000

## Stage 2 - Final / Revised Bid Value (post clarification / negotiation, if any)

Post-technical-qualification price negotiation round conducted as per GSPCL negotiation policy (bidder within 5% of L1). Bidder revised Total Base Price downward from ₹19.40 Cr to ₹18.60 Cr vide Letter HES/2026/112 dated 18-Mar-2026.

Final Total Base Price: ₹18,60,00,000   |   GST @ 13.8%: ₹2,56,68,000   |   Final Total Bid Value: ₹21,16,68,000

# 7. Remarks / Evaluation Committee Notes

Highest technical score overall; price revised down significantly after negotiation. Inverter efficiency deviation remains open pending committee decision on waiver.