Circuit Breakers India Corp.

CIN: U31909GJ2012PTC069215  |  Registered Office: Rajkot, Gujraat  |  Established: 2012

TECHNICAL & PRICE BID SUBMISSION
for
Tender Ref. GSETCL/SS-MORBI/2026/EPC-021
Design, Engineering, Supply, Erection, Testing and Commissioning of 132kV/33kV, 2x40 MVA Grid Substation at Morbi, Gujraat

| Field | Details |
| --- | --- |
| Bidder Reference | RESPONSE_DOC_S3 |
| Company Name | Circuit Breakers India Corp. |
| Date of Submission | 20-Feb-2026 |
| Overall Status (Evaluation Committee) | DISQUALIFIED AT ELIGIBILITY SCREENING (Multiple Grounds) |

# Table of Contents

1. Cover Letter & Company Profile

2. Eligibility Compliance Statement

3. Financial Standing

4. Detailed Project Experience (incl. 4.1 Individual Project Write-ups)

5. Design Basis & Engineering Philosophy

6. Power Transformer - Technical Specification

7. Protection & Control System - Relay Schedule

7A. 132kV Circuit Breaker Specification

7B. CT/PT Specification

7C. Isolators & Earth Switches Specification

7D. 33kV Switchgear Specification

7E. SCADA/RTU Specification

7F. DC Battery & Charger Specification

7G. Power & Control Cabling Specification

7H. Civil & Structural Works - Design Narrative

8. Equipment OEM / Approved Vendor Compliance

9. Quality Assurance Plan (QAP) - Inspection & Test Points

10. Health, Safety & Environment (HSE) Plan

11. Project Execution Methodology

12. Detailed Project Schedule

13. Manpower Deployment Plan

14. Plant, Machinery & Equipment Deployment

15. Mandatory Spares List

16. Testing & Commissioning Protocol

16A. Project Risk Register

16B. Terms & Conditions Compliance Matrix

16C. Key Personnel Profiles

16D. Sub-Vendor & OEM Profiles

17. Training & Warranty / Defect Liability

18. Deviations from Tender Requirements

19. Clarifications Sought & Bidder Responses

20. Priced Bill of Quantities (BOQ) - Stage 1 (Initial)

21. Priced Bill of Quantities (BOQ) - Stage 2 (Final)

22. Payment Terms Compliance Statement

23. List of Annexures

24. Compliance Undertaking

25. Evaluation Committee Remarks

# 1. Cover Letter & Company Profile

Circuit Breakers India Corp. confirms having read and fully understood the Scope of Work, Eligibility Criteria, Technical Requirements, Commercial Requirements, Evaluation Criteria, and General Terms & Conditions set out in Tender Document GSETCL/SS-MORBI/2026/EPC-021, and hereby submits its offer for the Design, Engineering, Supply, Erection, Testing and Commissioning of the 132kV/33kV, 2x40 MVA Grid Substation at Morbi, Gujraat, on a turnkey basis, on the terms set out in this bid.

Circuit Breakers India Corp., headquartered at Rajkot, Gujraat, was established in 2012 and has since built a portfolio of EHV substation EPC projects across Gujraat for state transmission utilities, industrial clients, and Indian Railways. The company operates its own in-house engineering design cell, project management team, and site execution force, supplemented by long-term relationships with GSETCL Approved Vendor List (AVL) OEMs for major equipment supply.

The organizational structure for this project will be headed by a dedicated Project Manager reporting to the company's Head of EHV Projects, with functional support from Design Engineering, Quality Assurance, HSE, Planning & Contracts, and Procurement departments operating out of the Rajkot, Gujraat corporate office, in addition to the dedicated site team described in Section 13.

# 2. Eligibility Compliance Statement

| Criteria | Bidder Submission |
| --- | --- |
| EC-1: Average Annual Turnover (last 3 FY) | ₹44.8 Cr / ₹47.1 Cr / ₹48.9 Cr ¦ Average: ₹46.93 Cr |
| EC-2: Relevant Experience (132kV+ substations) | 2 qualifying project(s) submitted - see Section 4 for details |
| EC-3: Net Worth | ₹19.4 Cr (positive, per FY 2024-25 audited statement) |
| EC-4: Quality Certifications (ISO) | ISO 9001:2015, ISO 14001:2015 valid and submitted; ISO 45001:2018 submitted but certificate shows scope limited to 'Manufacturing' and excludes 'Erection & Commissioning Services' |
| EC-5: Statutory Registrations / Electrical Contractor License | Electrical Contractor License Grade A No. GJ/EC/A/2019/00456, valid to Aug 2027 |
| EC-6: OEM Approval (Transformer / Breaker / Relay) | Transformer: BHEL - GSETCL AVL Rev.14, Sl.No. 1 ¦ Breaker: ABB India Ltd. - GSETCL AVL Rev.14, Sl.No. 5 ¦ Relay: ABB (RED670 series) - GSETCL AVL Rev.14, Sl.No. 4 |
| EC-8: EMD | ₹1,05,00,000 Bank Guarantee, Union Bank of India, valid 210 days - SHORTFALL of ₹15,00,000 against required ₹1,20,00,000 |
| Overall Eligibility Determination | NON-COMPLIANT - Average turnover ₹46.93 Cr is below the mandatory ₹50 Cr threshold (EC-1 failed); only 2 qualifying substation projects of 132kV+ submitted against the required minimum of 3 (EC-2 failed); ISO 45001 scope exclusion (EC-4 partial non-compliance); EMD short by ₹15,00,000 (EC-8 failed) |

# 3. Financial Standing

The financial statements submitted include audited Balance Sheets and Profit & Loss Accounts for FY 2022-23, 2023-24 and 2024-25, along with a Chartered Accountant's certificate confirming average annual turnover and a Banker's Solvency Certificate confirming a minimum solvency of ₹20 Crore. A summary of key financial indicators is presented below.

| Financial Parameter | FY 2022-23 | FY 2023-24 | FY 2024-25 |
| --- | --- | --- | --- |
| Annual Turnover | ₹44.8 Cr | ₹47.1 Cr | ₹48.9 Cr |
| Net Profit (after tax) | Refer audited P&L (Annexure-F) | Refer audited P&L (Annexure-F) | Refer audited P&L (Annexure-F) |
| Net Worth | Refer Annexure-F | Refer Annexure-F | ₹19.4 Cr (positive, per FY 2024-25 audited statement) |
| Current Ratio | 1.4 | 1.5 | 1.5 |
| Debt-Equity Ratio | 0.8 | 0.7 | 0.6 |

# 4. Detailed Project Experience

The following table lists the bidder's relevant substation project experience submitted in support of Eligibility Criterion EC-2 and the technical evaluation of project experience (25 marks). Projects marked with an asterisk (*) are below the 132kV voltage-class threshold specified in EC-2 and are included for information only; they do not count toward eligibility qualification.

| Project Name | Location | Capacity/Voltage | Client | Year | Scope Summary |
| --- | --- | --- | --- | --- | --- |
| 132kV GSS Bhachau * | Kutch, Gujraat | 132/33kV, 2x20 MVA | GSETCL | 2021 | Turnkey EPC of grid substation including AIS switchyard and control building. |
| 132kV GSS Halvad * | Surendranagar, Gujraat | 132/33kV, 1x25 MVA | GSETCL | 2020 | Design, supply and erection of new substation with numerical protection scheme. |
| 220kV GSS Rajula | Amreli, Gujraat | 220/132kV, 2x100 MVA | GSETCL | 2022 | EPC of 220kV substation, largest capacity project in bidder's portfolio. |
| 132kV GSS Tharad * | Banaskantha, Gujraat | 132/33kV, 2x40 MVA | GSETCL | 2023 | Full turnkey EPC identical scope to present tender, commissioned on schedule. |
| 132kV GSS Dahod Extension * | Dahod, Gujraat | 132/33kV, 1x20 MVA (extension) | GSETCL | 2019 | Extension of existing substation with new bay and protection upgrade. |
| 132kV GSS Wankaner | Morbi, Gujraat | 132/33kV, 2x31.5 MVA | GSETCL | 2022 | New grid substation EPC including SCADA integration with SLDC. |
| 132kV Industrial Substation, Dahej * | Bharuch, Gujraat | 132/33kV, 2x50 MVA | Private Industrial Client | 2021 | Captive substation for chemical SEZ, GIS switchyard configuration. |
| 132kV GSS Modasa * | Aravalli, Gujraat | 132/33kV, 1x40 MVA | GSETCL | 2020 | Substation EPC with control room civil works and 33kV switchgear. |
| 220kV GSS Sanand * | Ahmedabad, Gujraat | 220/132/33kV, 2x160 MVA | GSETCL | 2023 | Major 3-winding transformer substation, largest single project by value. |
| 132kV GSS Bagasara * | Amreli, Gujraat | 132/33kV, 1x25 MVA | GSETCL | 2018 | Grid substation with conventional AIS switchyard. |
| 132kV Railway Traction Substation, Palanpur * | Banaskantha, Gujraat | 132/25kV, 2x21.6 MVA | Indian Railways | 2022 | Traction substation for railway electrification project. |
| 132kV GSS Kalol * | Gandhinagar, Gujraat | 132/33kV, 2x40 MVA | GSETCL | 2024 | Recently commissioned substation, identical technical scope to present tender. |
| 132kV GSS Anjar * | Kutch, Gujraat | 132/33kV, 1x31.5 MVA | GSETCL | 2019 | EPC of substation in seismic zone with special foundation design. |
| 66kV GSS Idar * | Sabarkantha, Gujraat | 66/11kV, 2x10 MVA | GSETCL | 2017 | Smaller-capacity substation, below 132kV eligibility threshold. |
| 33kV Distribution Substation, Junagadh * | Junagadh, Gujraat | 33/11kV, 2x8 MVA | PGVCL | 2018 | Distribution-level substation, below 132kV eligibility threshold. |

Total qualifying (132kV+) projects submitted by Circuit Breakers India Corp.: 2. Detailed completion certificates, client reference letters, and work orders for each qualifying project are enclosed as Annexure-C.

## 4.1 Individual Project Reference Write-ups

## 132kV GSS Bhachau (below EC-2 voltage threshold)

Client: GSETCL  |  Location: Kutch, Gujraat  |  Capacity/Voltage Class: 132/33kV, 2x20 MVA  |  Year of Completion: 2021

Turnkey EPC of grid substation including AIS switchyard and control building. Circuit Breakers India Corp. was engaged as the Contractor for this project, responsible for detailed engineering, equipment supply coordination, civil and electrical erection, and testing & commissioning through to successful energization. The project was executed as a smaller-scope reference assignment, included here to demonstrate the bidder's broader substation execution capability. A completion certificate and client reference letter for this project are enclosed in Annexure-C, and referees are available for direct verification by GSETCL upon request.

## 132kV GSS Halvad (below EC-2 voltage threshold)

Client: GSETCL  |  Location: Surendranagar, Gujraat  |  Capacity/Voltage Class: 132/33kV, 1x25 MVA  |  Year of Completion: 2020

Design, supply and erection of new substation with numerical protection scheme. Circuit Breakers India Corp. was engaged as the Contractor for this project, responsible for detailed engineering, equipment supply coordination, civil and electrical erection, and testing & commissioning through to successful energization. The project was executed as a smaller-scope reference assignment, included here to demonstrate the bidder's broader substation execution capability. A completion certificate and client reference letter for this project are enclosed in Annexure-C, and referees are available for direct verification by GSETCL upon request.

## 220kV GSS Rajula

Client: GSETCL  |  Location: Amreli, Gujraat  |  Capacity/Voltage Class: 220/132kV, 2x100 MVA  |  Year of Completion: 2022

EPC of 220kV substation, largest capacity project in bidder's portfolio. Circuit Breakers India Corp. was engaged as the Turnkey EPC Contractor for this project, responsible for detailed engineering, equipment supply coordination, civil and electrical erection, and testing & commissioning through to successful energization. The project was executed in full compliance with the client's technical specifications and within the contractually agreed schedule. A completion certificate and client reference letter for this project are enclosed in Annexure-C, and referees are available for direct verification by GSETCL upon request.

## 132kV GSS Tharad (below EC-2 voltage threshold)

Client: GSETCL  |  Location: Banaskantha, Gujraat  |  Capacity/Voltage Class: 132/33kV, 2x40 MVA  |  Year of Completion: 2023

Full turnkey EPC identical scope to present tender, commissioned on schedule. Circuit Breakers India Corp. was engaged as the Contractor for this project, responsible for detailed engineering, equipment supply coordination, civil and electrical erection, and testing & commissioning through to successful energization. The project was executed as a smaller-scope reference assignment, included here to demonstrate the bidder's broader substation execution capability. A completion certificate and client reference letter for this project are enclosed in Annexure-C, and referees are available for direct verification by GSETCL upon request.

## 132kV GSS Dahod Extension (below EC-2 voltage threshold)

Client: GSETCL  |  Location: Dahod, Gujraat  |  Capacity/Voltage Class: 132/33kV, 1x20 MVA (extension)  |  Year of Completion: 2019

Extension of existing substation with new bay and protection upgrade. Circuit Breakers India Corp. was engaged as the Contractor for this project, responsible for detailed engineering, equipment supply coordination, civil and electrical erection, and testing & commissioning through to successful energization. The project was executed as a smaller-scope reference assignment, included here to demonstrate the bidder's broader substation execution capability. A completion certificate and client reference letter for this project are enclosed in Annexure-C, and referees are available for direct verification by GSETCL upon request.

## 132kV GSS Wankaner

Client: GSETCL  |  Location: Morbi, Gujraat  |  Capacity/Voltage Class: 132/33kV, 2x31.5 MVA  |  Year of Completion: 2022

New grid substation EPC including SCADA integration with SLDC. Circuit Breakers India Corp. was engaged as the Turnkey EPC Contractor for this project, responsible for detailed engineering, equipment supply coordination, civil and electrical erection, and testing & commissioning through to successful energization. The project was executed in full compliance with the client's technical specifications and within the contractually agreed schedule. A completion certificate and client reference letter for this project are enclosed in Annexure-C, and referees are available for direct verification by GSETCL upon request.

## 132kV Industrial Substation, Dahej (below EC-2 voltage threshold)

Client: Private Industrial Client  |  Location: Bharuch, Gujraat  |  Capacity/Voltage Class: 132/33kV, 2x50 MVA  |  Year of Completion: 2021

Captive substation for chemical SEZ, GIS switchyard configuration. Circuit Breakers India Corp. was engaged as the Contractor for this project, responsible for detailed engineering, equipment supply coordination, civil and electrical erection, and testing & commissioning through to successful energization. The project was executed as a smaller-scope reference assignment, included here to demonstrate the bidder's broader substation execution capability. A completion certificate and client reference letter for this project are enclosed in Annexure-C, and referees are available for direct verification by GSETCL upon request.

## 132kV GSS Modasa (below EC-2 voltage threshold)

Client: GSETCL  |  Location: Aravalli, Gujraat  |  Capacity/Voltage Class: 132/33kV, 1x40 MVA  |  Year of Completion: 2020

Substation EPC with control room civil works and 33kV switchgear. Circuit Breakers India Corp. was engaged as the Contractor for this project, responsible for detailed engineering, equipment supply coordination, civil and electrical erection, and testing & commissioning through to successful energization. The project was executed as a smaller-scope reference assignment, included here to demonstrate the bidder's broader substation execution capability. A completion certificate and client reference letter for this project are enclosed in Annexure-C, and referees are available for direct verification by GSETCL upon request.

## 220kV GSS Sanand (below EC-2 voltage threshold)

Client: GSETCL  |  Location: Ahmedabad, Gujraat  |  Capacity/Voltage Class: 220/132/33kV, 2x160 MVA  |  Year of Completion: 2023

Major 3-winding transformer substation, largest single project by value. Circuit Breakers India Corp. was engaged as the Contractor for this project, responsible for detailed engineering, equipment supply coordination, civil and electrical erection, and testing & commissioning through to successful energization. The project was executed as a smaller-scope reference assignment, included here to demonstrate the bidder's broader substation execution capability. A completion certificate and client reference letter for this project are enclosed in Annexure-C, and referees are available for direct verification by GSETCL upon request.

## 132kV GSS Bagasara (below EC-2 voltage threshold)

Client: GSETCL  |  Location: Amreli, Gujraat  |  Capacity/Voltage Class: 132/33kV, 1x25 MVA  |  Year of Completion: 2018

Grid substation with conventional AIS switchyard. Circuit Breakers India Corp. was engaged as the Contractor for this project, responsible for detailed engineering, equipment supply coordination, civil and electrical erection, and testing & commissioning through to successful energization. The project was executed as a smaller-scope reference assignment, included here to demonstrate the bidder's broader substation execution capability. A completion certificate and client reference letter for this project are enclosed in Annexure-C, and referees are available for direct verification by GSETCL upon request.

## 132kV Railway Traction Substation, Palanpur (below EC-2 voltage threshold)

Client: Indian Railways  |  Location: Banaskantha, Gujraat  |  Capacity/Voltage Class: 132/25kV, 2x21.6 MVA  |  Year of Completion: 2022

Traction substation for railway electrification project. Circuit Breakers India Corp. was engaged as the Contractor for this project, responsible for detailed engineering, equipment supply coordination, civil and electrical erection, and testing & commissioning through to successful energization. The project was executed as a smaller-scope reference assignment, included here to demonstrate the bidder's broader substation execution capability. A completion certificate and client reference letter for this project are enclosed in Annexure-C, and referees are available for direct verification by GSETCL upon request.

## 132kV GSS Kalol (below EC-2 voltage threshold)

Client: GSETCL  |  Location: Gandhinagar, Gujraat  |  Capacity/Voltage Class: 132/33kV, 2x40 MVA  |  Year of Completion: 2024

Recently commissioned substation, identical technical scope to present tender. Circuit Breakers India Corp. was engaged as the Contractor for this project, responsible for detailed engineering, equipment supply coordination, civil and electrical erection, and testing & commissioning through to successful energization. The project was executed as a smaller-scope reference assignment, included here to demonstrate the bidder's broader substation execution capability. A completion certificate and client reference letter for this project are enclosed in Annexure-C, and referees are available for direct verification by GSETCL upon request.

## 132kV GSS Anjar (below EC-2 voltage threshold)

Client: GSETCL  |  Location: Kutch, Gujraat  |  Capacity/Voltage Class: 132/33kV, 1x31.5 MVA  |  Year of Completion: 2019

EPC of substation in seismic zone with special foundation design. Circuit Breakers India Corp. was engaged as the Contractor for this project, responsible for detailed engineering, equipment supply coordination, civil and electrical erection, and testing & commissioning through to successful energization. The project was executed as a smaller-scope reference assignment, included here to demonstrate the bidder's broader substation execution capability. A completion certificate and client reference letter for this project are enclosed in Annexure-C, and referees are available for direct verification by GSETCL upon request.

## 66kV GSS Idar (below EC-2 voltage threshold)

Client: GSETCL  |  Location: Sabarkantha, Gujraat  |  Capacity/Voltage Class: 66/11kV, 2x10 MVA  |  Year of Completion: 2017

Smaller-capacity substation, below 132kV eligibility threshold. Circuit Breakers India Corp. was engaged as the Contractor for this project, responsible for detailed engineering, equipment supply coordination, civil and electrical erection, and testing & commissioning through to successful energization. The project was executed as a smaller-scope reference assignment, included here to demonstrate the bidder's broader substation execution capability. A completion certificate and client reference letter for this project are enclosed in Annexure-C, and referees are available for direct verification by GSETCL upon request.

## 33kV Distribution Substation, Junagadh (below EC-2 voltage threshold)

Client: PGVCL  |  Location: Junagadh, Gujraat  |  Capacity/Voltage Class: 33/11kV, 2x8 MVA  |  Year of Completion: 2018

Distribution-level substation, below 132kV eligibility threshold. Circuit Breakers India Corp. was engaged as the Contractor for this project, responsible for detailed engineering, equipment supply coordination, civil and electrical erection, and testing & commissioning through to successful energization. The project was executed as a smaller-scope reference assignment, included here to demonstrate the bidder's broader substation execution capability. A completion certificate and client reference letter for this project are enclosed in Annexure-C, and referees are available for direct verification by GSETCL upon request.

# 5. Design Basis & Engineering Philosophy

Circuit Breakers India Corp. has carried out preliminary engineering studies for the proposed 132kV/33kV, 2x40 MVA Grid Substation at Morbi, based on the site data, load forecast, and short-circuit level indicated in the Tender Document, and on the bidder's own site visit conducted during the pre-bid period. The design basis adopted is summarized in this section, and is consistent with Central Electricity Authority (CEA) Regulations, relevant Indian Standards (IS 3043, IS 2026, IS 2705, IS 3156), and GSETCL's standard technical specifications and General Technical Requirements (GTR).

The site soil investigation indicates a bearing capacity in the range applicable for isolated/raft foundations for the transformer plinths and 132kV bay structures, subject to confirmation through the detailed geotechnical investigation to be carried out during the mobilization phase. Seismic zone considerations for the Morbi region (Zone IV, per IS 1893) have been incorporated into the structural design philosophy, with appropriate ductile detailing for RCC elements and bracing for steel structures.

The switchyard layout has been developed on a single-bus, sectionalized configuration for the 132kV side (as specified), with adequate clearances per IS 5613 and CEA Safety Regulations for equipment maintenance, vehicular movement, and future bay extension. The 33kV switchgear is proposed to be housed indoors in an air-conditioned switchgear room within the control room building, to minimize environmental exposure and maintenance requirements over the plant life.

Protection philosophy is based on primary and backup protection redundancy for all 132kV feeders and the power transformers, using numerical relays compliant with IEC 61850 for station bus communication, enabling future SCADA/automation scalability. Differential protection is proposed for both the 132kV line and the power transformers, backed up by distance and time-graded overcurrent/earth-fault protection respectively.

The earthing system has been sized to achieve a grid resistance not exceeding 1 ohm and to safely dissipate the maximum anticipated fault current, with step and touch potentials maintained within IEEE 80 / IS 3043 safe limits at all accessible locations within and around the switchyard boundary.

# 6. Power Transformer - Technical Specification

Proposed OEM: BHEL - GSETCL AVL Rev.14, Sl.No. 1. Guaranteed temperature rise: Top oil 44°C / Winding 49°C over ambient (within limit). The detailed guaranteed technical particulars (GTP) offered against each Tender-specified parameter are tabulated below.

| Parameter | Tender Requirement / Bidder's Offer |
| --- | --- |
| Rated Capacity | 40 MVA (each, x2 Nos.) |
| Voltage Ratio | 132/33 kV |
| Vector Group | Dyn11 |
| Cooling | ONAN/ONAF |
| OLTC Range | ±10 x 1.5% (On-load, motorized) |
| Impedance @ 75°C | 10.5% (on 40 MVA base) |
| Top Oil Temp Rise | ≤ 45°C over ambient |
| Winding Temp Rise | ≤ 50°C over ambient |
| Insulation Level (HV) | BIL 650 kV, PF 275 kV |
| Insulation Level (LV) | BIL 170 kV, PF 70 kV |
| No-Load Loss | ≤ 22 kW (guaranteed) |
| Load Loss @ 75°C | ≤ 145 kW (guaranteed) |
| Noise Level | ≤ 68 dB(A) at 1m |
| Core Material | CRGO M4 or better, laser scribed |
| Bushings (HV) | Condenser type, OIP, 800A |
| Bushings (LV) | Condenser type, OIP, 2000A |
| Tap Changer Type | On-Load, resistor transition, motor drive |
| Winding Material | Copper, continuously transposed conductor |
| Oil Type | Uninhibited mineral insulating oil, IS 335 |
| Fire Protection | HV Water Spray / Nitrogen Injection Fire Protection System |

# 7. Protection & Control System - Relay Schedule

Proposed protection relay OEM: ABB (RED670 series) - GSETCL AVL Rev.14, Sl.No. 4. The complete protection and control philosophy, including relay function assignment and quantities, is summarized below; detailed protection coordination study and relay setting calculations are enclosed as Annexure-D.

| Protection Function | ANSI/IEC Device No. | Quantity |
| --- | --- | --- |
| 132kV Line Differential Protection | 87L | 2 |
| 132kV Distance Protection | 21 | 2 |
| Transformer Differential Protection | 87T | 2 |
| Transformer REF Protection | 64REF | 2 |
| O/C & E/F Protection (132kV) | 50/51, 50N/51N | 4 |
| O/C & E/F Protection (33kV) | 50/51, 50N/51N | 12 |
| Breaker Failure Protection | 50BF | 4 |
| Auto Reclose | 79 | 2 |
| Bus Bar Protection (132kV) | 87B | 1 |
| Under/Over Voltage Protection | 27/59 | 4 |
| Under/Over Frequency Protection | 81U/81O | 2 |
| Transformer Overload/RTCC | 49/OLTC | 2 |
| Restricted Earth Fault (33kV side) | 64REF-LV | 2 |
| Synchro-check Relay | 25 | 2 |
| Disturbance & Fault Recorder | DFR | 1 |

# 7A. 132kV SF6 Circuit Breaker - Technical Specification

Proposed OEM: ABB India Ltd. - GSETCL AVL Rev.14, Sl.No. 5. Guaranteed breaking capacity offered: 132kV, 2000A, 40kA for 3 sec (meets TR-3). Detailed guaranteed technical particulars are tabulated below.

| Parameter | Tender Requirement / Bidder's Offer |
| --- | --- |
| Rated Voltage | 145 kV |
| Rated Current | 2000 A |
| Rated Short Circuit Breaking Current | 40 kA for 3 sec |
| Rated Short Circuit Making Current | 100 kA (peak) |
| Number of Poles | 3, single/three-pole operated |
| Interrupting Medium | SF6 gas, puffer type |
| Operating Mechanism | Spring-charged, motor wound |
| Rated Operating Sequence | O - 0.3s - CO - 3min - CO |
| First Pole to Clear Factor | 1.3 |
| Rated Line Charging Breaking Current | As per IEC 62271-100 |
| SF6 Gas Pressure (rated) | 6.0 bar (abs) at 20°C |
| SF6 Density Monitor | Provided, with alarm & lockout contacts |
| Auto-Reclose Duty | Suitable for single/three-phase auto-reclose |
| Creepage Distance | ≥ 25mm/kV (heavily polluted zone) |
| Type Test Certificates | As per IEC 62271-100, CPRI/ERDA tested |

# 7B. Current & Potential Transformers - Technical Specification

Proposed OEM: as per Approved Vendor List cross-reference in Annexure-E. Guaranteed particulars for 132kV CTs and PTs are tabulated below.

| Parameter | Tender Requirement / Bidder's Offer |
| --- | --- |
| CT Ratio (Primary/Secondary) | 600-1200/1/1 A (multi-ratio) |
| CT Accuracy Class - Metering | 0.2S |
| CT Accuracy Class - Protection | 5P20 |
| CT Rated Burden | 30 VA (metering) / 30 VA (protection) |
| CT Short Time Rating | 40 kA for 3 sec |
| PT Ratio (Primary/Secondary) | 132/√3 kV / 110/√3 - 110/3 V |
| PT Accuracy Class - Metering | 0.2 |
| PT Accuracy Class - Protection | 3P |
| PT Rated Burden | 150 VA |
| Insulation Level | BIL 650kV, PF 275kV |
| Type | Oil-filled, hermetically sealed, inverted type |
| Type Test Certificates | As per IS 2705 / IS 3156, CPRI tested |

# 7C. Isolators & Earth Switches - Technical Specification

| Parameter | Tender Requirement / Bidder's Offer |
| --- | --- |
| Type | Double break / Pantograph, motorized |
| Rated Voltage | 145 kV |
| Rated Current | 1250 A |
| Short Time Withstand Current | 40 kA for 3 sec |
| Earth Switch | Integral, interlocked with main isolator |
| Operating Mechanism | Motor operated with local/remote/manual override |
| Interlocking Scheme | Electrical & mechanical, key-interlocked with associated CB |
| Type Test Certificates | As per IEC 62271-102 |

# 7D. 33kV Indoor Switchgear - Technical Specification

| Parameter | Tender Requirement / Bidder's Offer |
| --- | --- |
| Type | Metal-clad, indoor, floor-mounted, single front |
| Rated Voltage | 36 kV |
| Rated Current (Bus/Feeder) | 1250 A |
| Rated Short Circuit Current | 25 kA for 3 sec |
| Breaking Technique | Vacuum Circuit Breaker (VCB) |
| Operating Mechanism | Spring-charged, motor wound, trip-free |
| Internal Arc Classification | IAC AFLR, 25kA, 1 sec (per IEC 62271-200) |
| Degree of Protection | IP4X (compartment), IP2X (external) |
| Busbar Material | Electrolytic copper, insulated/sleeved |
| Partial Discharge Level | ≤ 10 pC at 1.1 Un |
| Interlocking | Fully interlocked (5-function type) |
| Metering & Protection | Numerical multifunction relay per panel with IEC 61850 port |
| Panel Construction | CRCA sheet steel, powder coated, compartmentalized |
| Type Test Certificates | As per IEC 62271-200, CPRI/ERDA tested |

# 7E. SCADA / RTU System - Technical Specification

| Parameter | Tender Requirement / Bidder's Offer |
| --- | --- |
| Protocol - Station Bus | IEC 61850 (GOOSE & MMS) |
| Protocol - SLDC Interface | IEC 60870-5-104 |
| RTU/Gateway Redundancy | Dual redundant, hot-standby |
| HMI | Local SCADA HMI with single-line mimic, alarm/event logging |
| Time Synchronization | GPS-based, IRIG-B / NTP |
| Data Retention | Minimum 1 year event/alarm history, local storage |
| Cyber Security | Role-based access control, firewall between station bus & WAN |
| Communication Media to SLDC | OPGW/PLCC as available, with backup |
| Disturbance Recording | Integrated DFR with COMTRADE export |
| Engineering Workstation | 1 No., with configuration software license (perpetual) |

# 7F. DC Battery & Charger System - Technical Specification

| Parameter | Tender Requirement / Bidder's Offer |
| --- | --- |
| Type | VRLA (Valve Regulated Lead Acid) |
| Voltage | 220V DC (110 cells nominal) |
| Capacity | 300 AH, 10-hour rate |
| Design Life | 15 years minimum |
| Charger Type | Dual (Float-cum-Boost), thyristor/IGBT controlled |
| Charger Rating | 220V DC, 30A (each) |
| Battery Monitoring | Cell voltage monitoring with alarm for low/high voltage |
| Enclosure | Dedicated, ventilated battery room with acid-resistant flooring |

# 7G. Power & Control Cabling - Technical Specification

| Parameter | Tender Requirement / Bidder's Offer |
| --- | --- |
| Power Cable Type | XLPE insulated, armoured, 33kV grade |
| Conductor | Stranded aluminium/copper as specified per circuit |
| Control Cable Type | PVC insulated, armoured, 1.1kV grade |
| Fire Retardant Rating | FRLS (Fire Retardant Low Smoke) |
| Cable Laying Method | Cable trench with tray, and direct buried for select runs |
| Cable Jointing | Heat-shrink / cold-shrink kits, OEM-certified jointers |
| Cable Testing | VLF withstand test (power cables), IR + continuity (control cables) |
| Cable Identification | Numbered ferrules at both ends as per approved cable schedule |

# 7H. Civil & Structural Works - Design Narrative

The control room building is proposed as a single-storey RCC-framed structure comprising a relay & control panel room, battery room, SCADA/communication room, store, and administrative office, designed for a minimum service life of 40 years. Equipment foundations for the power transformers and 132kV bay structures are designed as isolated RCC footings sized for the static and dynamic (short-circuit force, wind, seismic) loads specified in the relevant IS codes, with oil containment/soak pits provided beneath each transformer plinth per environmental norms.

Structural steel for the 132kV switchyard gantries and equipment support structures is proposed in hot-dip galvanized MS sections (minimum 86 microns galvanization per IS 4759), designed for the site wind zone and seismic zone as applicable, with bolted (non-welded) site connections to facilitate quality control and future maintenance.

Cable trenches are proposed in RCC construction with removable chequered-plate/RCC cover slabs, sized to accommodate the full cable schedule with 25% spare capacity for future cables, and sloped for drainage into the site's storm-water system to prevent water accumulation.

# 8. Equipment OEM / Approved Vendor Compliance

| Component | Proposed OEM / Make |
| --- | --- |
| Power Transformer (132/33kV, 40 MVA) | BHEL - GSETCL AVL Rev.14, Sl.No. 1 |
| 132kV SF6 Circuit Breaker | ABB India Ltd. - GSETCL AVL Rev.14, Sl.No. 5 |
| 132kV Current Transformer | As per GSETCL Approved Vendor List Rev.14 (details in Annexure-E) |
| 132kV Potential Transformer | As per GSETCL Approved Vendor List Rev.14 (details in Annexure-E) |
| 132kV Isolator with Earth Switch | As per GSETCL Approved Vendor List Rev.14 (details in Annexure-E) |
| 132kV Lightning Arrester | As per GSETCL Approved Vendor List Rev.14 (details in Annexure-E) |
| 33kV Indoor VCB Switchgear Panel | As per GSETCL Approved Vendor List Rev.14 (details in Annexure-E) |
| Numerical Protection Relays | ABB (RED670 series) - GSETCL AVL Rev.14, Sl.No. 4 |
| SCADA/RTU System | As per GSETCL Approved Vendor List Rev.14 (details in Annexure-E) |
| Control & Relay Panels (CRP) | As per GSETCL Approved Vendor List Rev.14 (details in Annexure-E) |
| Battery Bank (220V DC, VRLA) | As per GSETCL Approved Vendor List Rev.14 (details in Annexure-E) |
| Battery Charger (Dual, Float-cum-Boost) | As per GSETCL Approved Vendor List Rev.14 (details in Annexure-E) |
| Power & Control Cables (XLPE) | As per GSETCL Approved Vendor List Rev.14 (details in Annexure-E) |
| Structural Steel (Galvanized) | As per GSETCL Approved Vendor List Rev.14 (details in Annexure-E) |
| Earthing Conductor (GI/Copper) | As per GSETCL Approved Vendor List Rev.14 (details in Annexure-E) |

Circuit Breaker guaranteed rating offered: 132kV, 2000A, 40kA for 3 sec (meets TR-3).

# 9. Quality Assurance Plan (QAP) - Inspection & Test Points

Quality Assurance for this project will be governed by a project-specific Quality Assurance Plan (QAP), submitted for GSETCL approval within 30 days of LOA, covering incoming material inspection, in-process manufacturing inspection (at OEM works), routine and type testing, and site erection/testing quality checkpoints. Hold points and witness points requiring GSETCL / Third-Party Inspection Agency (TPIA) presence are identified in the detailed QAP. The summary inspection and test plan is presented below.

| S.No. | Inspection / Test Point | Hold/Witness/Review Classification |
| --- | --- | --- |
| 1 | Incoming inspection - CRGO core steel (mill TC verification) | Hold Point - GSETCL/TPIA witness mandatory before proceeding |
| 2 | Incoming inspection - copper conductor (purity & dimension check) | Witness Point - GSETCL/TPIA may witness on notice |
| 3 | Incoming inspection - transformer oil (BDV, moisture content) | Review Point - documentary review by QA Engineer, record maintained in QA dossier |
| 4 | Core building & lamination stacking inspection | Hold Point - GSETCL/TPIA witness mandatory before proceeding |
| 5 | Winding process inspection (turns, insulation wrap) | Witness Point - GSETCL/TPIA may witness on notice |
| 6 | Core-coil assembly inspection | Review Point - documentary review by QA Engineer, record maintained in QA dossier |
| 7 | Vacuum drying process record review | Hold Point - GSETCL/TPIA witness mandatory before proceeding |
| 8 | Tank fabrication & painting inspection (DFT check) | Witness Point - GSETCL/TPIA may witness on notice |
| 9 | Routine test - Ratio test (all taps) | Review Point - documentary review by QA Engineer, record maintained in QA dossier |
| 10 | Routine test - Winding resistance measurement | Hold Point - GSETCL/TPIA witness mandatory before proceeding |
| 11 | Routine test - Insulation resistance (IR) & Polarization Index | Witness Point - GSETCL/TPIA may witness on notice |
| 12 | Routine test - Tan Delta / Capacitance measurement | Review Point - documentary review by QA Engineer, record maintained in QA dossier |
| 13 | Routine test - Impulse withstand test (sample basis) | Hold Point - GSETCL/TPIA witness mandatory before proceeding |
| 14 | Routine test - Temperature rise test | Witness Point - GSETCL/TPIA may witness on notice |
| 15 | Routine test - Short circuit withstand test (type test certificate review) | Review Point - documentary review by QA Engineer, record maintained in QA dossier |
| 16 | 132kV SF6 Circuit Breaker - mechanical operation test | Hold Point - GSETCL/TPIA witness mandatory before proceeding |
| 17 | 132kV SF6 Circuit Breaker - SF6 gas leakage test | Witness Point - GSETCL/TPIA may witness on notice |
| 18 | CT/PT - ratio & polarity test | Review Point - documentary review by QA Engineer, record maintained in QA dossier |
| 19 | CT/PT - excitation characteristic test | Hold Point - GSETCL/TPIA witness mandatory before proceeding |
| 20 | Numerical relay - functional/scheme logic test | Witness Point - GSETCL/TPIA may witness on notice |
| 21 | Numerical relay - IEC 61850 GOOSE interoperability test | Review Point - documentary review by QA Engineer, record maintained in QA dossier |
| 22 | Control cable - continuity & insulation test | Hold Point - GSETCL/TPIA witness mandatory before proceeding |
| 23 | Power cable - HV DC/VLF withstand test | Witness Point - GSETCL/TPIA may witness on notice |
| 24 | Earthing system - resistance measurement (fall-of-potential method) | Review Point - documentary review by QA Engineer, record maintained in QA dossier |
| 25 | Structural steel - galvanization thickness (DFT) check | Hold Point - GSETCL/TPIA witness mandatory before proceeding |
| 26 | Civil works - concrete cube compressive strength test | Witness Point - GSETCL/TPIA may witness on notice |
| 27 | Civil works - soil compaction test (proctor density) | Review Point - documentary review by QA Engineer, record maintained in QA dossier |
| 28 | Battery bank - capacity discharge test | Hold Point - GSETCL/TPIA witness mandatory before proceeding |
| 29 | SCADA/RTU - protocol conformance test (IEC 60870-5-104) | Witness Point - GSETCL/TPIA may witness on notice |
| 30 | Final inspection & pre-dispatch inspection (PDI) by client-nominated TPI | Review Point - documentary review by QA Engineer, record maintained in QA dossier |

# 10. Health, Safety & Environment (HSE) Plan

Circuit Breakers India Corp. maintains a documented Health, Safety & Environment Management System aligned with ISO 45001:2018 and ISO 14001:2015, and applies this system to all EHV substation project sites. The HSE Plan for this project will be site-specific, reviewed and approved by GSETCL prior to mobilization, and enforced through a dedicated site HSE team reporting independently to the Project Manager. The following checklist summarizes the key HSE controls to be implemented throughout the project duration, from mobilization through to commissioning and handover.

| S.No. | HSE Control Measure | Responsibility |
| --- | --- | --- |
| 1 | Site-specific HSE Plan approved before mobilization | Site HSE Officer |
| 2 | Daily Tool Box Talk (TBT) records maintained | Project Manager |
| 3 | Permit-to-Work system for hot works, excavation, working at height | Site Engineer (all disciplines) |
| 4 | PPE compliance monitoring (helmets, safety harness, insulated gloves) | HSE Officer + Site Supervisors |
| 5 | Lock-Out Tag-Out (LOTO) procedure for live equipment isolation | Site HSE Officer |
| 6 | First-aid station and trained first-aiders on site | Project Manager |
| 7 | Fire extinguishers positioned at all high-risk zones | Site Engineer (all disciplines) |
| 8 | Emergency response & evacuation plan displayed and rehearsed | HSE Officer + Site Supervisors |
| 9 | Monthly safety audit and non-conformance tracking | Site HSE Officer |
| 10 | Incident/near-miss reporting and root-cause analysis (RCA) system | Project Manager |
| 11 | Crane & lifting equipment - third-party certification | Site Engineer (all disciplines) |
| 12 | Scaffold inspection tagging system | HSE Officer + Site Supervisors |
| 13 | Excavation safety - shoring/trench box for depth > 1.5m | Site HSE Officer |
| 14 | Electrical safety - earthing of temporary construction power | Project Manager |
| 15 | Environmental management - dust and noise control | Site Engineer (all disciplines) |
| 16 | Waste management - segregation and disposal as per local regulations | HSE Officer + Site Supervisors |
| 17 | Worker health check-up (pre-employment and periodic) | Site HSE Officer |
| 18 | Safety induction training for all site personnel | Project Manager |
| 19 | Zero Lost-Time Injury (LTI) target with monthly HSE KPI reporting | Site Engineer (all disciplines) |
| 20 | COVID/communicable disease protocol (as applicable) | HSE Officer + Site Supervisors |

# 11. Project Execution Methodology

Circuit Breakers India Corp. proposes to execute this project using a parallel-path methodology wherein civil works, long-lead equipment procurement (power transformers, 132kV switchgear), and detailed engineering proceed concurrently from Day 1 of mobilization, in order to compress the overall project schedule while managing interface risk through a dedicated Planning Engineer using a detailed Level-3 project schedule. Monthly progress review meetings will be held with GSETCL, supported by weekly internal progress tracking and a formal Change/Deviation register.

Key execution phases comprise: (i) Mobilization & Engineering, (ii) Civil Works, (iii) Equipment Procurement & Manufacturing, (iv) Erection & Installation, (v) Testing, Pre-Commissioning & Commissioning, and (vi) Handover & Training. Interfaces between civil and electrical erection teams will be managed through a joint interface schedule reviewed weekly. A dedicated Document Control system will track drawing revisions and approval status throughout the project.

# 12. Detailed Project Schedule

The overall project duration proposed is 330 days from Letter of Award (LOA) to Commercial Commissioning, against the Tender's indicative schedule of 300 days (Section 6 of BASE_DOC). The detailed activity-wise schedule (Level-2) is presented below; a Level-3 bar chart schedule is enclosed as Annexure-G.

| Activity | Planned Completion (Days from LOA) |
| --- | --- |
| Letter of Award (LOA) issuance | 0 |
| Contract signing & kick-off meeting | 8 |
| Mobilization of site team & establishment | 17 |
| Topographic & geotechnical survey | 22 |
| Preparation of Design Basis Report (DBR) | 28 |
| General Arrangement (GA) drawing submission | 33 |
| Single Line Diagram (SLD) submission | 35 |
| Protection scheme drawing submission | 39 |
| Earthing layout drawing submission | 39 |
| Cable schedule & routing drawing submission | 42 |
| Client review & drawing approval cycle | 50 |
| Site clearance & leveling | 55 |
| Boundary wall construction start | 61 |
| Control room building - foundation | 66 |
| Control room building - superstructure | 99 |
| Control room building - roofing & finishing | 132 |
| Equipment foundation - transformer plinth | 77 |
| Equipment foundation - 132kV bay structures | 94 |
| Equipment foundation - 33kV switchgear room | 105 |
| Cable trench civil works | 110 |
| Internal road & drainage works | 121 |
| Placing of Power Transformer order (OEM) | 22 |
| Power Transformer - design approval (OEM) | 50 |
| Power Transformer - manufacturing | 165 |
| Power Transformer - factory testing (FAT) | 176 |
| Power Transformer - dispatch to site | 187 |
| Placing of 132kV switchgear order (OEM) | 22 |
| 132kV switchgear - manufacturing & FAT | 154 |
| 132kV switchgear - dispatch to site | 165 |
| Placing of 33kV switchgear order | 28 |
| 33kV switchgear - manufacturing & FAT | 143 |
| 33kV switchgear - dispatch to site | 154 |
| Placing of protection relay & SCADA order | 33 |
| 132kV structure erection | 215 |
| Transformer erection & oil filling | 220 |
| 132kV equipment erection (CB, CT, PT, isolators) | 231 |
| Bus-bar stringing | 237 |
| 33kV switchgear installation (indoor) | 242 |
| Control & Relay Panel (CRP) installation | 248 |
| Battery bank & DC system installation | 248 |
| Cabling - power cables | 253 |
| Cabling - control cables | 259 |
| Earthing grid installation & testing | 220 |
| Protection relay configuration & scheme testing | 270 |
| SCADA/RTU installation & IEC 60870-5-104 integration | 275 |
| Pre-commissioning checks (all sub-systems) | 292 |
| Testing & commissioning with State grid (joint with GSETCL/SLDC) | 314 |
| Punch-list closure & as-built documentation | 325 |
| Handover & training of GSETCL O&M staff | 328 |
| Commercial commissioning | 330 |

# 13. Manpower Deployment Plan

The following table summarizes the peak manpower deployment plan proposed for this project across all disciplines and phases of work.

| Role / Designation | Qualification / Experience | Peak Headcount |
| --- | --- | --- |
| Project Manager | B.E./B.Tech (Electrical), 15+ yrs EHV substation experience | 1 |
| Deputy Project Manager | B.E. Electrical, 10+ yrs | 1 |
| Site Engineer - Civil | B.E. Civil, 8+ yrs | 3 |
| Site Engineer - Electrical (HV) | B.E. Electrical, 8+ yrs | 4 |
| Site Engineer - Protection & Control | B.E./Dip. Electrical, 6+ yrs relay experience | 2 |
| QA/QC Engineer | B.E. with NDT/QC certification | 2 |
| HSE Officer | Diploma with NEBOSH/IOSH certification | 2 |
| Planning Engineer | B.E. with Primavera/MS Project expertise | 1 |
| Design Engineer - Civil | B.E. Civil, structural design experience | 2 |
| Design Engineer - Electrical | B.E. Electrical, SLD/protection design | 2 |
| Draughtsman (AutoCAD) | Diploma, AutoCAD/PLS-CADD proficient | 3 |
| Store & Logistics In-charge | Graduate, ERP/inventory management | 1 |
| Foreman - Civil | ITI/Diploma, 10+ yrs | 3 |
| Foreman - Electrical | ITI/Diploma, 10+ yrs | 4 |
| Skilled Electricians | ITI Electrician, licensed | 13 |
| Skilled Welders | ITI Welder, certified | 8 |
| Riggers & Crane Operators | Certified riggers/operators | 6 |
| Civil Masons & Carpenters | Skilled trade | 16 |
| Unskilled Labour | Local workforce | 26 |
| Testing & Commissioning Engineer | B.E. Electrical, relay/testing specialist | 3 |
| SCADA/RTU Engineer | B.E./B.Tech, IEC 61850/60870-5-104 experience | 2 |
| Surveyor | Diploma, total station/GPS survey | 1 |
| Store Assistant | Graduate | 2 |
| Security Supervisor | Ex-serviceman preferred | 2 |
| Security Guards | Trained security personnel | 6 |
| Document Controller | Graduate, document management | 1 |
| Admin & HR Coordinator | Graduate | 1 |
| Vehicle & Transport In-charge | Valid commercial license | 2 |
| First Aid Attendant | Certified first-aider/paramedic | 1 |
| Environment Engineer | B.E./M.Sc. Environmental Science | 1 |

# 14. Plant, Machinery & Equipment Deployment

| S.No. | Construction Plant / Testing Equipment | Ownership / Source |
| --- | --- | --- |
| 1 | Mobile Crane 50T capacity | Company owned |
| 2 | Mobile Crane 25T capacity | Hired, on long-term rental from empanelled vendor |
| 3 | Hydra Crane 14T capacity | Company owned |
| 4 | Transformer trailer (low-bed, 60T capacity) | Hired, on long-term rental from empanelled vendor |
| 5 | Excavator (JCB) 0.9 cum | Company owned |
| 6 | Concrete Batching Plant (30 cum/hr) | Hired, on long-term rental from empanelled vendor |
| 7 | Concrete Transit Mixer (6 cum) | Company owned |
| 8 | Vibrator - Needle type | Hired, on long-term rental from empanelled vendor |
| 9 | DG Set 125 kVA (construction power) | Company owned |
| 10 | DG Set 62.5 kVA (backup) | Hired, on long-term rental from empanelled vendor |
| 11 | Cable Laying Machine / Winch | Company owned |
| 12 | HV Cable Jointing Kit | Hired, on long-term rental from empanelled vendor |
| 13 | Insulation Resistance (IR) Tester (5kV) | Company owned |
| 14 | Primary Injection Test Kit | Hired, on long-term rental from empanelled vendor |
| 15 | Secondary Injection Test Kit | Company owned |
| 16 | CT/PT Analyzer | Hired, on long-term rental from empanelled vendor |
| 17 | Sweep Frequency Response Analyzer (SFRA) | Company owned |
| 18 | Tan Delta Test Set | Hired, on long-term rental from empanelled vendor |
| 19 | Oil BDV Test Kit | Company owned |
| 20 | Earth Resistance Tester (Fall-of-Potential) | Hired, on long-term rental from empanelled vendor |

# 15. Mandatory Spares List

The following mandatory spares are offered as part of the Contract Price, for GSETCL's use during the 24-month Defect Liability Period and initial O&M phase; priced separately in the BOQ (Section 20/21, Item 57). Delivery of the complete spares list to GSETCL's designated store is proposed within 30 days of commissioning.

| S.No. | Spare Item | Quantity Offered |
| --- | --- | --- |
| 1 | 132kV CB spare trip/close coil | 1 |
| 2 | 132kV CB spare SF6 density monitor | 2 |
| 3 | CT/PT spare secondary terminal block | 3 |
| 4 | Numerical relay - spare unit (1 per type) | 1 |
| 5 | Battery cells - 10% spare capacity | 2 |
| 6 | Control cable - 5% spare length | 3 |
| 7 | Power cable - 3% spare length | 1 |
| 8 | OLTC spare contacts set | 2 |
| 9 | Transformer Buchholz relay - spare | 3 |
| 10 | Transformer oil - 500 litres reserve | 1 |
| 11 | Isolator spare operating mechanism | 2 |
| 12 | Lightning arrester - 2 spare units | 3 |
| 13 | SCADA/RTU - spare I/O card set | 1 |
| 14 | Cooling fan motor - spare set (transformer) | 2 |
| 15 | Gasket & sealing kit - transformer | 3 |
| 16 | Earthing clamps & connectors - spare set | 1 |
| 17 | Fuses & MCBs - assorted spare set | 2 |
| 18 | Indicating lamps & push buttons - spare set | 3 |
| 19 | Cable glands & lugs - assorted spare set | 1 |
| 20 | Auxiliary relays & timers - spare set | 2 |

# 16. Testing & Commissioning Protocol

| S.No. | Test / Check | Stage |
| --- | --- | --- |
| 1 | Insulation Resistance (IR) test on all equipment before energization | Factory (at OEM works, pre-dispatch) |
| 2 | High Voltage (HV) test on power & control cables (VLF/DC) | Factory (at OEM works, pre-dispatch) |
| 3 | Ratio & Polarity test on all CTs/PTs | Factory (at OEM works, pre-dispatch) |
| 4 | Ratio test on Power Transformer (all taps) | Factory (at OEM works, pre-dispatch) |
| 5 | Winding Resistance measurement on Power Transformer | Factory (at OEM works, pre-dispatch) |
| 6 | Magnetic balance & magnetizing current test | Factory (at OEM works, pre-dispatch) |
| 7 | Sweep Frequency Response Analysis (SFRA) - baseline | Factory (at OEM works, pre-dispatch) |
| 8 | Vector group verification | Factory (at OEM works, pre-dispatch) |
| 9 | Transformer oil - BDV, moisture (Karl Fischer), DGA (baseline) | Factory (at OEM works, pre-dispatch) |
| 10 | SF6 gas - moisture and purity test on Circuit Breakers | Site - Pre-commissioning |
| 11 | Circuit Breaker timing & contact resistance test | Site - Pre-commissioning |
| 12 | Relay - functional test as per approved scheme logic | Site - Pre-commissioning |
| 13 | Relay - GOOSE message verification (IEC 61850 station bus) | Site - Pre-commissioning |
| 14 | Protection scheme - end-to-end primary injection test | Site - Pre-commissioning |
| 15 | Bus bar - contact resistance (micro-ohmmeter) test | Site - Pre-commissioning |
| 16 | Earthing grid resistance measurement | Site - Pre-commissioning |
| 17 | Earth mat step & touch potential verification | Site - Pre-commissioning |
| 18 | Battery bank - capacity/discharge test | Site - Pre-commissioning |
| 19 | DC system - ripple and float voltage check | Site - Pre-commissioning |
| 20 | SCADA - point-to-point signal verification with SLDC | Site - Pre-commissioning |
| 21 | SCADA - IEC 60870-5-104 protocol conformance test | Site - Commissioning / Joint with GSETCL-SLDC |
| 22 | Synchronization check with grid (synchro-check relay verification) | Site - Commissioning / Joint with GSETCL-SLDC |
| 23 | Load trial run (minimum 72 hours continuous monitoring) | Site - Commissioning / Joint with GSETCL-SLDC |
| 24 | Thermo-vision (IR thermography) scan of all joints under load | Site - Commissioning / Joint with GSETCL-SLDC |
| 25 | Final punch-list inspection & joint commissioning certificate sign-off | Site - Commissioning / Joint with GSETCL-SLDC |

# 16A. Project Risk Register

The following risk register identifies the key risks anticipated for this project, their category, and the mitigation measures proposed by Circuit Breakers India Corp.. This register will be maintained and reviewed monthly throughout project execution as part of the Project Management Plan.

| Risk Description | Category | Mitigation Measure |
| --- | --- | --- |
| Delay in power transformer manufacturing/FAT due to OEM backlog | Schedule | Early order placement within 20 days of LOA; monthly OEM progress review; contractual OEM delivery penalty pass-through |
| Delay in statutory approvals (CEIG, forest/environment clearances if applicable) | Regulatory | Early liaison with GSETCL's regulatory cell; dedicated liaison engineer; parallel processing with civil works |
| Monsoon impact on civil works and cable trenching | Schedule | Civil works sequencing to front-load foundation work before monsoon; temporary drainage arrangements |
| Fault level/short circuit study deviation at site | Technical | Independent verification study to be conducted jointly with GSETCL Protection Cell during design phase |
| Non-availability of skilled HV jointers for 132kV cable works | Resource | Pre-booking of certified jointing crews from OEM-approved list; backup crew identified |
| Price escalation in steel/copper during execution | Commercial | Firm-price contract accepted; internal hedging through forward material booking at contract signing |
| Interface delay between civil and electrical erection teams | Coordination | Weekly joint interface meetings; single-point interface coordinator appointed |
| Grid outage window unavailability for final commissioning cut-over | Schedule | Early coordination with SLDC for outage planning; commissioning readiness 2 weeks in advance |
| Site law & order / land access issues | External | Local liaison office established; community engagement plan |
| COVID/pandemic-related workforce disruption | Resource | Contingency workforce pool identified; digital progress monitoring capability |
| Design changes requested by GSETCL during execution | Scope | Formal change control process with impact assessment on cost/schedule |
| Quality non-conformance at OEM works | Quality | TPIA witness at all critical hold points; NCR closure tracking system |
| Site accident/safety incident | Safety | Comprehensive HSE Plan (Section 10); daily TBT; zero-LTI target |
| Currency/import duty fluctuation on imported components | Commercial | Minimal import content; domestic AVL-approved OEMs preferred |
| Cyber-security vulnerability in SCADA/RTU integration | Technical | IEC 62443-aligned network segmentation; penetration testing before go-live |
| Land subsidence/soil bearing capacity deviation from assumption | Technical | Detailed geotechnical investigation in first 20 days; design contingency in foundation sizing |
| Key personnel attrition during project | Resource | Backup personnel identified for all key roles; knowledge transfer protocol |
| Third-party damage to underground utilities during excavation | External | Utility mapping survey before excavation; permit-to-work for all digging |
| Testing equipment calibration lapse | Quality | Calibration tracking register; only NABL-calibrated instruments used |
| Documentation/as-built drawing delay affecting handover | Administrative | Dedicated document controller; concurrent as-built markup during execution, not deferred to end |

# 16B. Terms & Conditions Compliance Matrix

The table below cross-references each major term of Section 7 (General Terms & Conditions) of the BASE_DOC against the bidder's compliance status.

| Clause | Requirement | Bidder Compliance |
| --- | --- | --- |
| Bid Validity | 150 days from Price Bid opening | Complied |
| Completion Period | 10 months (300 days) from LOA | Complied - see Section 12 for bidder's proposed schedule |
| Liquidated Damages | 0.5% of Contract Value per week, capped at 10% | Complied |
| Defect Liability Period | 24 months from commissioning | Complied |
| Performance Bank Guarantee | 5% of Contract Value within 15 days of LOA | Complied |
| Mobilization Advance | Max 10% against Bank Guarantee | Complied - advance to be claimed against equivalent BG |
| Price Basis | Firm, fixed price, FOR site, GST extra | Complied |
| Insurance | CAR + Third Party Liability for full contract duration | Complied - policy to be procured post-LOA |
| Dispute Resolution | Arbitration under Arbitration & Conciliation Act, 1996; seat Vadodara | Complied |
| Force Majeure | As per GSETCL General Conditions of Contract, Clause 22 | Complied |
| Taxes & Duties | GST extra at applicable rate; other duties included in quoted price | Complied |
| Sub-contracting | Only with prior written approval of GSETCL | Complied - no sub-contracting of core scope envisaged except specialist testing |
| Statutory Compliance (Labour) | EPF/ESI compliance for all site labour | Complied - monthly challans to be submitted with running bills |
| Safety Compliance | As per GSETCL Safety Code and Factories Act | Complied - see Section 10 HSE Plan |
| Confidentiality | Non-disclosure of GSETCL design/data to third parties | Complied |
| IPR | Drawings/designs prepared for this project vest with GSETCL | Complied |
| Termination for Convenience | GSETCL's right to terminate with notice, per GCC | Noted and accepted |
| Assignment | No assignment of contract without GSETCL's written consent | Complied |
| Inspection Rights | GSETCL/TPIA right to inspect at all stages including at sub-vendor works | Complied |
| Record Retention | Project records to be retained for 5 years post-DLP | Complied |

# 16C. Key Personnel Profiles

Brief profiles of the key personnel proposed to be deployed on this project are provided below. Detailed CVs, along with proof of qualification and past project involvement, are enclosed as part of the technical proposal.

## Project Manager

25+ years in EHV substation EPC; has led commissioning of 8 substations of 132kV and above across Western India.

This resource will be dedicated to the GSETCL Morbi project for its full duration (mobilization through handover) and will not be shared concurrently with any other ongoing project of Circuit Breakers India Corp. above 50% allocation, except during ramp-down phases as mutually agreed with GSETCL's Engineer-in-Charge.

## Design Head - Electrical

18 years in protection & control system design; certified in IEC 61850 system engineering.

This resource will be dedicated to the GSETCL Morbi project for its full duration (mobilization through handover) and will not be shared concurrently with any other ongoing project of Circuit Breakers India Corp. above 50% allocation, except during ramp-down phases as mutually agreed with GSETCL's Engineer-in-Charge.

## Design Head - Civil/Structural

16 years in industrial and substation civil/structural design; seismic design specialist.

This resource will be dedicated to the GSETCL Morbi project for its full duration (mobilization through handover) and will not be shared concurrently with any other ongoing project of Circuit Breakers India Corp. above 50% allocation, except during ramp-down phases as mutually agreed with GSETCL's Engineer-in-Charge.

## QA/QC Manager

14 years in electrical equipment quality assurance; ASNT Level II certified for NDT methods.

This resource will be dedicated to the GSETCL Morbi project for its full duration (mobilization through handover) and will not be shared concurrently with any other ongoing project of Circuit Breakers India Corp. above 50% allocation, except during ramp-down phases as mutually agreed with GSETCL's Engineer-in-Charge.

## HSE Manager

12 years in construction HSE; NEBOSH IGC certified; managed HSE for 5+ EHV projects without LTI.

This resource will be dedicated to the GSETCL Morbi project for its full duration (mobilization through handover) and will not be shared concurrently with any other ongoing project of Circuit Breakers India Corp. above 50% allocation, except during ramp-down phases as mutually agreed with GSETCL's Engineer-in-Charge.

## Planning & Contracts Manager

15 years in EPC project planning; Primavera P6 certified; experienced in FIDIC and GCC contract administration.

This resource will be dedicated to the GSETCL Morbi project for its full duration (mobilization through handover) and will not be shared concurrently with any other ongoing project of Circuit Breakers India Corp. above 50% allocation, except during ramp-down phases as mutually agreed with GSETCL's Engineer-in-Charge.

## Commissioning Engineer-in-Charge

20 years in substation testing & commissioning; has commissioned 15+ substations including SCADA integration.

This resource will be dedicated to the GSETCL Morbi project for its full duration (mobilization through handover) and will not be shared concurrently with any other ongoing project of Circuit Breakers India Corp. above 50% allocation, except during ramp-down phases as mutually agreed with GSETCL's Engineer-in-Charge.

## Procurement Manager

13 years in EHV equipment procurement; manages OEM relationships across transformer, switchgear and relay categories.

This resource will be dedicated to the GSETCL Morbi project for its full duration (mobilization through handover) and will not be shared concurrently with any other ongoing project of Circuit Breakers India Corp. above 50% allocation, except during ramp-down phases as mutually agreed with GSETCL's Engineer-in-Charge.

# 16D. Sub-Vendor & OEM Profiles

Circuit Breakers India Corp. maintains long-standing relationships with the equipment OEMs proposed for this project. A brief profile of each major sub-vendor/OEM proposed is provided below, along with their relevance to the GSETCL Approved Vendor List requirement (EC-6) where applicable.

## Power Transformer (132/33kV, 40 MVA)

This component will be sourced through a formal purchase order placed within 20 days of LOA, with design/drawing approval obtained from GSETCL prior to manufacture. Manufacturing will be subject to the inspection and test plan detailed in Section 9 (QAP), with hold points witnessed by GSETCL or its nominated Third-Party Inspection Agency as applicable. Standard OEM warranty terms will be passed through to GSETCL as described in Section 17.

Delivery lead time for this component is estimated at 4-6 months from date of order placement, factored into the detailed project schedule in Section 12. Payment to the sub-vendor/OEM will be released back-to-back with GSETCL's milestone payments to Circuit Breakers India Corp., ensuring no cash-flow-related delivery risk to the project.

## 132kV SF6 Circuit Breaker

This component will be sourced through a formal purchase order placed within 20 days of LOA, with design/drawing approval obtained from GSETCL prior to manufacture. Manufacturing will be subject to the inspection and test plan detailed in Section 9 (QAP), with hold points witnessed by GSETCL or its nominated Third-Party Inspection Agency as applicable. Standard OEM warranty terms will be passed through to GSETCL as described in Section 17.

Delivery lead time for this component is estimated at 4-6 months from date of order placement, factored into the detailed project schedule in Section 12. Payment to the sub-vendor/OEM will be released back-to-back with GSETCL's milestone payments to Circuit Breakers India Corp., ensuring no cash-flow-related delivery risk to the project.

## 132kV Current Transformer

This component will be sourced through a formal purchase order placed within 20 days of LOA, with design/drawing approval obtained from GSETCL prior to manufacture. Manufacturing will be subject to the inspection and test plan detailed in Section 9 (QAP), with hold points witnessed by GSETCL or its nominated Third-Party Inspection Agency as applicable. Standard OEM warranty terms will be passed through to GSETCL as described in Section 17.

Delivery lead time for this component is estimated at 4-6 months from date of order placement, factored into the detailed project schedule in Section 12. Payment to the sub-vendor/OEM will be released back-to-back with GSETCL's milestone payments to Circuit Breakers India Corp., ensuring no cash-flow-related delivery risk to the project.

## 132kV Potential Transformer

This component will be sourced through a formal purchase order placed within 20 days of LOA, with design/drawing approval obtained from GSETCL prior to manufacture. Manufacturing will be subject to the inspection and test plan detailed in Section 9 (QAP), with hold points witnessed by GSETCL or its nominated Third-Party Inspection Agency as applicable. Standard OEM warranty terms will be passed through to GSETCL as described in Section 17.

Delivery lead time for this component is estimated at 4-6 months from date of order placement, factored into the detailed project schedule in Section 12. Payment to the sub-vendor/OEM will be released back-to-back with GSETCL's milestone payments to Circuit Breakers India Corp., ensuring no cash-flow-related delivery risk to the project.

## 132kV Isolator with Earth Switch

This component will be sourced through a formal purchase order placed within 20 days of LOA, with design/drawing approval obtained from GSETCL prior to manufacture. Manufacturing will be subject to the inspection and test plan detailed in Section 9 (QAP), with hold points witnessed by GSETCL or its nominated Third-Party Inspection Agency as applicable. Standard OEM warranty terms will be passed through to GSETCL as described in Section 17.

Delivery lead time for this component is estimated at 4-6 months from date of order placement, factored into the detailed project schedule in Section 12. Payment to the sub-vendor/OEM will be released back-to-back with GSETCL's milestone payments to Circuit Breakers India Corp., ensuring no cash-flow-related delivery risk to the project.

## 132kV Lightning Arrester

This component will be sourced through a formal purchase order placed within 20 days of LOA, with design/drawing approval obtained from GSETCL prior to manufacture. Manufacturing will be subject to the inspection and test plan detailed in Section 9 (QAP), with hold points witnessed by GSETCL or its nominated Third-Party Inspection Agency as applicable. Standard OEM warranty terms will be passed through to GSETCL as described in Section 17.

Delivery lead time for this component is estimated at 4-6 months from date of order placement, factored into the detailed project schedule in Section 12. Payment to the sub-vendor/OEM will be released back-to-back with GSETCL's milestone payments to Circuit Breakers India Corp., ensuring no cash-flow-related delivery risk to the project.

## 33kV Indoor VCB Switchgear Panel

This component will be sourced through a formal purchase order placed within 20 days of LOA, with design/drawing approval obtained from GSETCL prior to manufacture. Manufacturing will be subject to the inspection and test plan detailed in Section 9 (QAP), with hold points witnessed by GSETCL or its nominated Third-Party Inspection Agency as applicable. Standard OEM warranty terms will be passed through to GSETCL as described in Section 17.

Delivery lead time for this component is estimated at 4-6 months from date of order placement, factored into the detailed project schedule in Section 12. Payment to the sub-vendor/OEM will be released back-to-back with GSETCL's milestone payments to Circuit Breakers India Corp., ensuring no cash-flow-related delivery risk to the project.

## Numerical Protection Relays

This component will be sourced through a formal purchase order placed within 20 days of LOA, with design/drawing approval obtained from GSETCL prior to manufacture. Manufacturing will be subject to the inspection and test plan detailed in Section 9 (QAP), with hold points witnessed by GSETCL or its nominated Third-Party Inspection Agency as applicable. Standard OEM warranty terms will be passed through to GSETCL as described in Section 17.

Delivery lead time for this component is estimated at 4-6 months from date of order placement, factored into the detailed project schedule in Section 12. Payment to the sub-vendor/OEM will be released back-to-back with GSETCL's milestone payments to Circuit Breakers India Corp., ensuring no cash-flow-related delivery risk to the project.

## SCADA/RTU System

This component will be sourced through a formal purchase order placed within 20 days of LOA, with design/drawing approval obtained from GSETCL prior to manufacture. Manufacturing will be subject to the inspection and test plan detailed in Section 9 (QAP), with hold points witnessed by GSETCL or its nominated Third-Party Inspection Agency as applicable. Standard OEM warranty terms will be passed through to GSETCL as described in Section 17.

Delivery lead time for this component is estimated at 4-6 months from date of order placement, factored into the detailed project schedule in Section 12. Payment to the sub-vendor/OEM will be released back-to-back with GSETCL's milestone payments to Circuit Breakers India Corp., ensuring no cash-flow-related delivery risk to the project.

## Control & Relay Panels (CRP)

This component will be sourced through a formal purchase order placed within 20 days of LOA, with design/drawing approval obtained from GSETCL prior to manufacture. Manufacturing will be subject to the inspection and test plan detailed in Section 9 (QAP), with hold points witnessed by GSETCL or its nominated Third-Party Inspection Agency as applicable. Standard OEM warranty terms will be passed through to GSETCL as described in Section 17.

Delivery lead time for this component is estimated at 4-6 months from date of order placement, factored into the detailed project schedule in Section 12. Payment to the sub-vendor/OEM will be released back-to-back with GSETCL's milestone payments to Circuit Breakers India Corp., ensuring no cash-flow-related delivery risk to the project.

## Battery Bank (220V DC, VRLA)

This component will be sourced through a formal purchase order placed within 20 days of LOA, with design/drawing approval obtained from GSETCL prior to manufacture. Manufacturing will be subject to the inspection and test plan detailed in Section 9 (QAP), with hold points witnessed by GSETCL or its nominated Third-Party Inspection Agency as applicable. Standard OEM warranty terms will be passed through to GSETCL as described in Section 17.

Delivery lead time for this component is estimated at 4-6 months from date of order placement, factored into the detailed project schedule in Section 12. Payment to the sub-vendor/OEM will be released back-to-back with GSETCL's milestone payments to Circuit Breakers India Corp., ensuring no cash-flow-related delivery risk to the project.

## Battery Charger (Dual, Float-cum-Boost)

This component will be sourced through a formal purchase order placed within 20 days of LOA, with design/drawing approval obtained from GSETCL prior to manufacture. Manufacturing will be subject to the inspection and test plan detailed in Section 9 (QAP), with hold points witnessed by GSETCL or its nominated Third-Party Inspection Agency as applicable. Standard OEM warranty terms will be passed through to GSETCL as described in Section 17.

Delivery lead time for this component is estimated at 4-6 months from date of order placement, factored into the detailed project schedule in Section 12. Payment to the sub-vendor/OEM will be released back-to-back with GSETCL's milestone payments to Circuit Breakers India Corp., ensuring no cash-flow-related delivery risk to the project.

## Power & Control Cables (XLPE)

This component will be sourced through a formal purchase order placed within 20 days of LOA, with design/drawing approval obtained from GSETCL prior to manufacture. Manufacturing will be subject to the inspection and test plan detailed in Section 9 (QAP), with hold points witnessed by GSETCL or its nominated Third-Party Inspection Agency as applicable. Standard OEM warranty terms will be passed through to GSETCL as described in Section 17.

Delivery lead time for this component is estimated at 4-6 months from date of order placement, factored into the detailed project schedule in Section 12. Payment to the sub-vendor/OEM will be released back-to-back with GSETCL's milestone payments to Circuit Breakers India Corp., ensuring no cash-flow-related delivery risk to the project.

## Structural Steel (Galvanized)

This component will be sourced through a formal purchase order placed within 20 days of LOA, with design/drawing approval obtained from GSETCL prior to manufacture. Manufacturing will be subject to the inspection and test plan detailed in Section 9 (QAP), with hold points witnessed by GSETCL or its nominated Third-Party Inspection Agency as applicable. Standard OEM warranty terms will be passed through to GSETCL as described in Section 17.

Delivery lead time for this component is estimated at 4-6 months from date of order placement, factored into the detailed project schedule in Section 12. Payment to the sub-vendor/OEM will be released back-to-back with GSETCL's milestone payments to Circuit Breakers India Corp., ensuring no cash-flow-related delivery risk to the project.

## Earthing Conductor (GI/Copper)

This component will be sourced through a formal purchase order placed within 20 days of LOA, with design/drawing approval obtained from GSETCL prior to manufacture. Manufacturing will be subject to the inspection and test plan detailed in Section 9 (QAP), with hold points witnessed by GSETCL or its nominated Third-Party Inspection Agency as applicable. Standard OEM warranty terms will be passed through to GSETCL as described in Section 17.

Delivery lead time for this component is estimated at 4-6 months from date of order placement, factored into the detailed project schedule in Section 12. Payment to the sub-vendor/OEM will be released back-to-back with GSETCL's milestone payments to Circuit Breakers India Corp., ensuring no cash-flow-related delivery risk to the project.

# 16E. Approved Makes List (Bulk Materials)

In accordance with standard EPC practice and GSETCL's General Technical Requirements, the following Approved Makes List is proposed for bulk construction materials not separately covered by the OEM equipment specifications above. Any substitution during execution will be subject to GSETCL's prior written approval.

| Material Category | Approved Makes (any one) |
| --- | --- |
| Cement (OPC 43/53 Grade) | Ultratech / Ambuja / ACC |
| TMT Reinforcement Steel | TATA Tiscon / SAIL / JSW |
| Structural Steel Sections | SAIL / JSPL / Jindal |
| Ready Mix Concrete | Ultratech RMC / Local NABL-tested plant |
| Waterproofing Compound | Dr. Fixit / Fosroc |
| Paints - Structural Steel | Asian Paints / Berger / Jotun |
| GI Pipes/Fittings | Tata / Jindal Hissar |
| XLPE Power Cables | Polycab / KEI / Havells |
| Control Cables | Polycab / KEI / Universal |
| Cable Trays | Legrand / Indiana / Slotco |
| Cable Glands & Lugs | Comet / Dowells / Braco |
| MCBs/MCCBs | Schneider / L&T / ABB |
| Push Buttons & Indicating Lamps | L&T / Siemens / Teknic |
| Terminal Blocks | Wago / Phoenix Contact / Elmex |
| Junction Boxes | Baliga / Sudhir / Flameproof (as applicable) |
| Illumination Fixtures | Philips / Bajaj / Crompton |
| Earthing Strips (GI/Copper) | As per BIS-approved rolling mills |
| Nuts, Bolts & Fasteners (HDG) | Unbrako / Sundram / GKW |
| Anti-Termite Treatment Chemicals | Bayer / BASF |
| HDPE Pipes (drainage) | Supreme / Finolex |
| Chequered Plates (trench cover) | SAIL / JSW |
| Fire Extinguishers | Ceasefire / Safex / Minimax |
| HVAC Equipment (control room) | Voltas / Blue Star / Daikin |
| DG Set | Cummins / Kirloskar / Mahindra Powerol |
| Batteries (VRLA) | Exide / Amara Raja / HBL |
| Battery Chargers | AMARA RAJA / HBL Power / Statcon |
| Numerical Relays | As proposed in Section 7/8 - ABB (RED670 series) - GSETCL AVL Rev.14, Sl.No. 4 |
| Power Transformer | As proposed in Section 6 - BHEL - GSETCL AVL Rev.14, Sl.No. 1 |
| 132kV Circuit Breaker | As proposed in Section 7A - ABB India Ltd. - GSETCL AVL Rev.14, Sl.No. 5 |
| CCTV Cameras & NVR | Hikvision / CP Plus / Bosch |
| Fire Alarm Panel | Honeywell / Siemens / Ravel |
| Cable Jointing Kits | Raychem / 3M / Densons |
| Insulators (post/string) | WS Insulators / Aditya Birla / Modern Insulators |
| Bus Bar Conductor | Hindalco (Aluminium) / Hindustan Copper |
| Danger/Caution Signage | As per CEA Safety Regulations, locally sourced |
| Site Fencing (chain-link/RCC) | Local approved vendor |
| Sand & Aggregate | Locally sourced, tested for grading & silt content |
| Bricks/Blocks | Locally sourced, IS-compliant |
| Roofing Sheets | Tata Bluescope / JSW / Everest |
| Doors & Windows (Control Room) | Fenesta / local fabricated, powder-coated aluminium |
| Floor Tiles / Anti-static Flooring (relay room) | Kajaria / Somany / 3M anti-static |

# 16F. Drawing & Document Submission Schedule

The following drawings and documents will be submitted for GSETCL's review and approval as per the timeline indicated (days from LOA), consistent with the overall project schedule in Section 12.

| Document / Drawing | Target Submission (Days from LOA) |
| --- | --- |
| General Arrangement (GA) Drawing - Switchyard | 20 |
| General Arrangement (GA) Drawing - Control Room Building | 26 |
| Single Line Diagram (SLD) | 32 |
| Protection & Metering Scheme Drawings | 38 |
| Relay Setting Calculation Report | 44 |
| Earthing Layout & Calculation Report | 50 |
| Lightning Protection Layout | 56 |
| Cable Schedule & Routing Drawing | 62 |
| Foundation Design & GA - Power Transformer | 68 |
| Foundation Design & GA - 132kV Bay Structures | 74 |
| Structural Steel Fabrication Drawings | 80 |
| Bill of Quantities - Civil Works (Detailed) | 86 |
| Power Transformer - GTP & GA Drawing (OEM) | 92 |
| 132kV CB - GTP & GA Drawing (OEM) | 98 |
| CT/PT - GTP & GA Drawing (OEM) | 104 |
| 33kV Switchgear - GTP & GA Drawing (OEM) | 110 |
| SCADA/RTU - System Architecture Drawing | 116 |
| SCADA/RTU - I/O List & Signal Schedule | 122 |
| Battery Sizing Calculation | 128 |
| DC Distribution Scheme Drawing | 134 |
| AC Distribution Scheme Drawing | 140 |
| Fire Protection System Layout | 146 |
| HVAC Layout - Control Room | 152 |
| Illumination Layout - Switchyard | 158 |
| Quality Assurance Plan (QAP) - Detailed | 164 |
| Inspection & Test Plan (ITP) - Equipment-wise | 170 |
| Method Statements - Civil Works | 176 |
| Method Statements - Electrical Erection | 182 |
| Commissioning Test Procedure Document | 188 |
| As-Built Drawing Package (Final) | 194 |

# 16G. Statutory Approvals & Liaison Responsibility Matrix

| Approval / Clearance | Responsibility | Target Timeline |
| --- | --- | --- |
| Chief Electrical Inspector to Government (CEIG) approval | Contractor to prepare application; GSETCL to co-sign as owner | Prior to commissioning |
| Grid connectivity approval from SLDC | Contractor to submit technical data; GSETCL to lead coordination | T + 250 days |
| Environmental clearance (if applicable, site-specific) | GSETCL (owner's responsibility); Contractor to support documentation | Prior to civil works commencement |
| Factory/labour license for site establishment | Contractor | Prior to mobilization |
| Explosives license (if DG fuel storage above threshold) | Contractor | Prior to DG installation |
| Fire NOC from local fire department | Contractor to apply; GSETCL to support as owner | Prior to commissioning |
| Local municipal building permission (control room) | Contractor to prepare; GSETCL to co-sign as owner | Prior to civil works commencement |
| Type approval / BIS certification verification for equipment | Contractor | Prior to equipment dispatch |
| Import license (for any imported components, if applicable) | Contractor | As applicable |
| Right-of-way / land access permissions | GSETCL (owner's responsibility) | Prior to mobilization |
| Traffic/road-cutting permission (for cable crossing, if any) | Contractor | As required during execution |
| Pollution Control Board consent (construction phase) | Contractor to support; GSETCL to lead | Prior to civil works commencement |
| Weighbridge/material testing lab accreditation verification | Contractor | Ongoing |
| Third-Party Inspection Agency (TPIA) appointment coordination | GSETCL to appoint; Contractor to coordinate schedule | Within 30 days of LOA |
| Insurance policy registration (CAR + TPL) | Contractor | Within 15 days of LOA |

# 17. Training & Warranty / Defect Liability

Circuit Breakers India Corp. will conduct a structured 2-week on-site training program for GSETCL's O&M personnel prior to handover, covering safe operating procedures, routine maintenance schedules, protection relay settings management, SCADA/RTU operation, and emergency response procedures. Training material, including an O&M manual specific to the commissioned equipment, will be provided in both English and Gujarati.

The Defect Liability Period (DLP) of 24 months from the date of commissioning, as required under Section 7 of the Tender Document, is accepted. During the DLP, Circuit Breakers India Corp. shall attend to any defect notified by GSETCL within 72 hours for critical faults (affecting substation availability) and within 7 days for non-critical faults, at no additional cost, subject to the defect not arising from GSETCL's own operational error, force majeure, or third-party damage.

Equipment-specific manufacturer warranties (power transformers, circuit breakers, relays) as offered by the respective OEMs, which in most cases extend beyond the 24-month contractual DLP, will be passed through to GSETCL along with the relevant OEM warranty certificates at the time of commissioning.

# 18. Deviations from Tender Requirements

| Clause / Requirement | Deviation Stated | Evaluation Committee Assessment |
| --- | --- | --- |
| Eligibility - Average Turnover (EC-1) | Quoted average turnover ₹46.93 Cr against required ₹50 Cr | Major - Disqualifying |
| Eligibility - Relevant Experience (EC-2) | Only 2 qualifying 132kV+ substation projects submitted (3 required, or 1x220kV alternate not independently satisfied) | Major - Disqualifying |
| ISO 45001:2018 Scope (EC-4) | Certificate scope excludes 'Erection & Commissioning Services', covering only 'Manufacturing' | Major - Disqualifying (certificate scope does not cover the services being tendered) |
| EMD Amount (EC-8) | EMD submitted ₹1,05,00,000 against required ₹1,20,00,000 (₹15,00,000 shortfall) | Major - Non-responsive per GCC unless rectified within cure period |

# 19. Clarifications Sought & Bidder Responses

| Ref. | Clarification Sought by GSETCL | Bidder Response |
| --- | --- | --- |
| CL-1 | Submit additional qualifying project experience or clarify basis of claiming EC-2 compliance | Bidder cited 2 additional projects below 132kV voltage class (66kV and 33kV) as 'equivalent complexity'; these do not meet the voltage-class threshold specified in EC-2 and were not accepted |
| CL-2 | Rectify EMD shortfall of ₹15,00,000 within the prescribed cure period | No additional EMD instrument was received within the cure period; shortfall remains unrectified as of the evaluation report date |
| CL-3 | Clarify ISO 45001:2018 certificate scope limitation | Bidder stated a scope-extension application is in progress with the certification body but could not provide a valid extended-scope certificate before bid evaluation closure |

# 20. Priced Bill of Quantities (BOQ) - Stage 1 (Initial Bid, submitted 20-Feb-2026)

| Description | Unit | Qty | Rate (₹) | Amount (₹) |
| --- | --- | --- | --- | --- |
| Site clearance, leveling and grading | sqm | 12000 | ₹95 | ₹11,40,000 |
| Earthwork excavation for foundations (ordinary soil) | cum | 2400 | ₹235 | ₹5,64,000 |
| Earthwork excavation for cable trenches | cum | 1600 | ₹269 | ₹4,30,400 |
| PCC M-10 for foundation bed | cum | 180 | ₹5,824 | ₹10,48,320 |
| RCC M-25 for equipment foundations | cum | 620 | ₹9,968 | ₹61,80,160 |
| RCC M-30 for control room building | cum | 480 | ₹10,752 | ₹51,60,960 |
| Structural steel fabrication & erection (galvanized) | MT | 145 | ₹1,43,360 | ₹2,07,87,200 |
| Boundary wall (RCC precast panel, 2.4m height) | rmt | 620 | ₹4,704 | ₹29,16,480 |
| Internal road (WBM + bituminous) | sqm | 3200 | ₹1,624 | ₹51,96,800 |
| Cable trench with RCC cover slabs | rmt | 850 | ₹7,616 | ₹64,73,600 |
| Control room building - civil (turnkey, incl. finishing) | sqm | 420 | ₹35,840 | ₹1,50,52,800 |
| Storm water drainage system | rmt | 480 | ₹2,072 | ₹9,94,560 |
| Rain water harvesting system | LS | 1 | ₹9,52,000 | ₹9,52,000 |
| Fire fighting system (hydrant + hose reel) | LS | 1 | ₹35,84,000 | ₹35,84,000 |
| Landscaping & site restoration | LS | 1 | ₹7,28,000 | ₹7,28,000 |
| Power Transformer 132/33kV, 40 MVA, ONAN/ONAF with OLTC | No. | 2 | ₹4,76,00,000 | ₹9,52,00,000 |
| 132kV SF6 Circuit Breaker, 2000A, 40kA | No. | 6 | ₹43,12,000 | ₹2,58,72,000 |
| 132kV Current Transformer, Class 0.2S/5P20 | No. | 18 | ₹4,31,200 | ₹77,61,600 |
| 132kV Potential Transformer, Class 0.2/3P | No. | 6 | ₹4,76,000 | ₹28,56,000 |
| 132kV Isolator with earth switch, motorized | No. | 10 | ₹12,88,000 | ₹1,28,80,000 |
| 132kV Lightning Arrester | No. | 8 | ₹3,19,200 | ₹25,53,600 |
| 132kV Bus-bar structure & fittings (per bay) | No. | 4 | ₹20,72,000 | ₹82,88,000 |
| 132kV bay complete (structure, clamps, hardware) | No. | 4 | ₹24,64,000 | ₹98,56,000 |
| 132kV wave trap & coupling capacitor (PLCC) | Set | 2 | ₹16,24,000 | ₹32,48,000 |
| 33kV Indoor VCB Switchgear Panel (metal-clad, 1250A) | No. | 12 | ₹18,48,000 | ₹2,21,76,000 |
| 33kV Bus Coupler Panel | No. | 1 | ₹16,24,000 | ₹16,24,000 |
| 33kV Cable end termination kit | No. | 12 | ₹72,800 | ₹8,73,600 |
| Numerical protection relay - differential/distance (87/21) | No. | 6 | ₹5,43,200 | ₹32,59,200 |
| Numerical protection relay - O/C, E/F (50/51) | No. | 16 | ₹2,07,200 | ₹33,15,200 |
| Numerical relay - bus bar protection (87B) | No. | 1 | ₹14,00,000 | ₹14,00,000 |
| Control & Relay Panel (CRP), free-standing | No. | 8 | ₹10,64,000 | ₹85,12,000 |
| SCADA/RTU system with IEC 60870-5-104 gateway | LS | 1 | ₹95,20,000 | ₹95,20,000 |
| Battery bank 220V DC, 300AH VRLA with charger (dual) | Set | 1 | ₹31,92,000 | ₹31,92,000 |
| AC/DC Distribution Board | Set | 2 | ₹7,28,000 | ₹14,56,000 |
| Power cable, XLPE, 3C x 400 sqmm, 33kV grade | rmt | 850 | ₹3,584 | ₹30,46,400 |
| Power cable, XLPE, 3C x 240 sqmm, 33kV grade | rmt | 620 | ₹2,688 | ₹16,66,560 |
| Control cable, PVC, multi-core (various sizes) | rmt | 12000 | ₹207 | ₹24,84,000 |
| Cable tray & accessories (GI, perforated) | rmt | 1400 | ₹1,064 | ₹14,89,600 |
| HV cable jointing kits (33kV) | No. | 24 | ₹50,400 | ₹12,09,600 |
| LT power & lighting works (control room) | LS | 1 | ₹20,72,000 | ₹20,72,000 |
| Earthing conductor - GI strip 75x10mm | rmt | 3200 | ₹470 | ₹15,04,000 |
| Earthing conductor - copper strip (equipment) | rmt | 850 | ₹1,400 | ₹11,90,000 |
| Earth electrode - GI pipe/plate type | No. | 65 | ₹9,520 | ₹6,18,800 |
| Earth pit with maintenance-free treatment | No. | 65 | ₹14,000 | ₹9,10,000 |
| Risers & equipment earthing connections | LS | 1 | ₹10,64,000 | ₹10,64,000 |
| Illumination system - switchyard (flood lights + poles) | LS | 1 | ₹24,64,000 | ₹24,64,000 |
| DG Set - permanent standby, 62.5 kVA | No. | 1 | ₹20,72,000 | ₹20,72,000 |
| Fire alarm & detection system - control room | LS | 1 | ₹16,24,000 | ₹16,24,000 |
| HVAC system for control room / relay room | LS | 1 | ₹21,84,000 | ₹21,84,000 |
| CCTV surveillance system | LS | 1 | ₹14,00,000 | ₹14,00,000 |
| Type testing charges (as applicable, sample basis) | LS | 1 | ₹20,72,000 | ₹20,72,000 |
| Routine testing charges - all equipment | LS | 1 | ₹14,00,000 | ₹14,00,000 |
| Third-party inspection (TPI) charges | LS | 1 | ₹10,64,000 | ₹10,64,000 |
| Pre-commissioning checks & test kits mobilization | LS | 1 | ₹16,24,000 | ₹16,24,000 |
| Commissioning assistance & grid synchronization support | LS | 1 | ₹20,72,000 | ₹20,72,000 |
| As-built drawings & O&M manual documentation | LS | 1 | ₹7,28,000 | ₹7,28,000 |
| Training of GSETCL O&M personnel (2 weeks, on-site) | LS | 1 | ₹5,04,000 | ₹5,04,000 |
| Mandatory spares (2-year DLP support) - Section 15 list | LS | 1 | ₹54,32,000 | ₹54,32,000 |
| Special tools & tackles for O&M | LS | 1 | ₹9,52,000 | ₹9,52,000 |
| Insurance (CAR + Third Party Liability) for full duration | LS | 1 | ₹27,44,000 | ₹27,44,000 |
| Mobilization & demobilization of construction equipment | LS | 1 | ₹18,48,000 | ₹18,48,000 |

Total Base Price (Stage 1): ₹34,24,91,440   |   GST @ 18%: ₹6,16,48,459   |   Total Bid Value (Stage 1): ₹40,41,39,899

# 21. Priced Bill of Quantities (BOQ) - Stage 2 (Final, post clarification / negotiation)

Price Bid was opened for record purposes as part of the standard two-envelope process, but is NOT considered for comparative evaluation or award, as the bid failed Eligibility Screening (Stage 1) on multiple mandatory criteria and does not proceed to Technical or Price Evaluation per Section 5 of the BASE_DOC.

| Description | Unit | Qty | Rate (₹) | Amount (₹) |
| --- | --- | --- | --- | --- |
| Site clearance, leveling and grading | sqm | 12000 | ₹95 | ₹11,40,000 |
| Earthwork excavation for foundations (ordinary soil) | cum | 2400 | ₹235 | ₹5,64,000 |
| Earthwork excavation for cable trenches | cum | 1600 | ₹269 | ₹4,30,400 |
| PCC M-10 for foundation bed | cum | 180 | ₹5,824 | ₹10,48,320 |
| RCC M-25 for equipment foundations | cum | 620 | ₹9,968 | ₹61,80,160 |
| RCC M-30 for control room building | cum | 480 | ₹10,752 | ₹51,60,960 |
| Structural steel fabrication & erection (galvanized) | MT | 145 | ₹1,43,360 | ₹2,07,87,200 |
| Boundary wall (RCC precast panel, 2.4m height) | rmt | 620 | ₹4,704 | ₹29,16,480 |
| Internal road (WBM + bituminous) | sqm | 3200 | ₹1,624 | ₹51,96,800 |
| Cable trench with RCC cover slabs | rmt | 850 | ₹7,616 | ₹64,73,600 |
| Control room building - civil (turnkey, incl. finishing) | sqm | 420 | ₹35,840 | ₹1,50,52,800 |
| Storm water drainage system | rmt | 480 | ₹2,072 | ₹9,94,560 |
| Rain water harvesting system | LS | 1 | ₹9,52,000 | ₹9,52,000 |
| Fire fighting system (hydrant + hose reel) | LS | 1 | ₹35,84,000 | ₹35,84,000 |
| Landscaping & site restoration | LS | 1 | ₹7,28,000 | ₹7,28,000 |
| Power Transformer 132/33kV, 40 MVA, ONAN/ONAF with OLTC | No. | 2 | ₹4,76,00,000 | ₹9,52,00,000 |
| 132kV SF6 Circuit Breaker, 2000A, 40kA | No. | 6 | ₹43,12,000 | ₹2,58,72,000 |
| 132kV Current Transformer, Class 0.2S/5P20 | No. | 18 | ₹4,31,200 | ₹77,61,600 |
| 132kV Potential Transformer, Class 0.2/3P | No. | 6 | ₹4,76,000 | ₹28,56,000 |
| 132kV Isolator with earth switch, motorized | No. | 10 | ₹12,88,000 | ₹1,28,80,000 |
| 132kV Lightning Arrester | No. | 8 | ₹3,19,200 | ₹25,53,600 |
| 132kV Bus-bar structure & fittings (per bay) | No. | 4 | ₹20,72,000 | ₹82,88,000 |
| 132kV bay complete (structure, clamps, hardware) | No. | 4 | ₹24,64,000 | ₹98,56,000 |
| 132kV wave trap & coupling capacitor (PLCC) | Set | 2 | ₹16,24,000 | ₹32,48,000 |
| 33kV Indoor VCB Switchgear Panel (metal-clad, 1250A) | No. | 12 | ₹18,48,000 | ₹2,21,76,000 |
| 33kV Bus Coupler Panel | No. | 1 | ₹16,24,000 | ₹16,24,000 |
| 33kV Cable end termination kit | No. | 12 | ₹72,800 | ₹8,73,600 |
| Numerical protection relay - differential/distance (87/21) | No. | 6 | ₹5,43,200 | ₹32,59,200 |
| Numerical protection relay - O/C, E/F (50/51) | No. | 16 | ₹2,07,200 | ₹33,15,200 |
| Numerical relay - bus bar protection (87B) | No. | 1 | ₹14,00,000 | ₹14,00,000 |
| Control & Relay Panel (CRP), free-standing | No. | 8 | ₹10,64,000 | ₹85,12,000 |
| SCADA/RTU system with IEC 60870-5-104 gateway | LS | 1 | ₹95,20,000 | ₹95,20,000 |
| Battery bank 220V DC, 300AH VRLA with charger (dual) | Set | 1 | ₹31,92,000 | ₹31,92,000 |
| AC/DC Distribution Board | Set | 2 | ₹7,28,000 | ₹14,56,000 |
| Power cable, XLPE, 3C x 400 sqmm, 33kV grade | rmt | 850 | ₹3,584 | ₹30,46,400 |
| Power cable, XLPE, 3C x 240 sqmm, 33kV grade | rmt | 620 | ₹2,688 | ₹16,66,560 |
| Control cable, PVC, multi-core (various sizes) | rmt | 12000 | ₹207 | ₹24,84,000 |
| Cable tray & accessories (GI, perforated) | rmt | 1400 | ₹1,064 | ₹14,89,600 |
| HV cable jointing kits (33kV) | No. | 24 | ₹50,400 | ₹12,09,600 |
| LT power & lighting works (control room) | LS | 1 | ₹20,72,000 | ₹20,72,000 |
| Earthing conductor - GI strip 75x10mm | rmt | 3200 | ₹470 | ₹15,04,000 |
| Earthing conductor - copper strip (equipment) | rmt | 850 | ₹1,400 | ₹11,90,000 |
| Earth electrode - GI pipe/plate type | No. | 65 | ₹9,520 | ₹6,18,800 |
| Earth pit with maintenance-free treatment | No. | 65 | ₹14,000 | ₹9,10,000 |
| Risers & equipment earthing connections | LS | 1 | ₹10,64,000 | ₹10,64,000 |
| Illumination system - switchyard (flood lights + poles) | LS | 1 | ₹24,64,000 | ₹24,64,000 |
| DG Set - permanent standby, 62.5 kVA | No. | 1 | ₹20,72,000 | ₹20,72,000 |
| Fire alarm & detection system - control room | LS | 1 | ₹16,24,000 | ₹16,24,000 |
| HVAC system for control room / relay room | LS | 1 | ₹21,84,000 | ₹21,84,000 |
| CCTV surveillance system | LS | 1 | ₹14,00,000 | ₹14,00,000 |
| Type testing charges (as applicable, sample basis) | LS | 1 | ₹20,72,000 | ₹20,72,000 |
| Routine testing charges - all equipment | LS | 1 | ₹14,00,000 | ₹14,00,000 |
| Third-party inspection (TPI) charges | LS | 1 | ₹10,64,000 | ₹10,64,000 |
| Pre-commissioning checks & test kits mobilization | LS | 1 | ₹16,24,000 | ₹16,24,000 |
| Commissioning assistance & grid synchronization support | LS | 1 | ₹20,72,000 | ₹20,72,000 |
| As-built drawings & O&M manual documentation | LS | 1 | ₹7,28,000 | ₹7,28,000 |
| Training of GSETCL O&M personnel (2 weeks, on-site) | LS | 1 | ₹5,04,000 | ₹5,04,000 |
| Mandatory spares (2-year DLP support) - Section 15 list | LS | 1 | ₹54,32,000 | ₹54,32,000 |
| Special tools & tackles for O&M | LS | 1 | ₹9,52,000 | ₹9,52,000 |
| Insurance (CAR + Third Party Liability) for full duration | LS | 1 | ₹27,44,000 | ₹27,44,000 |
| Mobilization & demobilization of construction equipment | LS | 1 | ₹18,48,000 | ₹18,48,000 |

Final Total Base Price (Stage 2): ₹34,24,91,440   |   GST @ 18%: ₹6,16,48,459   |   Final Total Bid Value (Stage 2): ₹40,41,39,899

# 22. Payment Terms Compliance Statement

Circuit Breakers India Corp. confirms acceptance of the Milestone Payment Schedule set out in Section 6 of the BASE_DOC, with payments released against each milestone certified by GSETCL's Engineer-in-Charge, subject to submission of corresponding invoices, test certificates, and (where applicable) statutory compliance documents (EPF/ESI challans for site labour). No mobilization advance beyond 10% of Contract Value against an equivalent Bank Guarantee is sought.

# 23. List of Annexures

- Annexure-A: Bid Submission Form (signed)

- Annexure-B: EMD Instrument (Bank Guarantee)

- Annexure-C: Project Completion Certificates & Client Reference Letters

- Annexure-D: Protection Coordination Study & Relay Setting Calculations (preliminary)

- Annexure-E: OEM Authorization Letters & Approved Vendor List Cross-Reference

- Annexure-F: Audited Financial Statements (FY 2022-23 to 2024-25) & CA Certificate

- Annexure-G: Level-3 Project Schedule (Bar Chart)

- Annexure-H: ISO 9001/14001/45001 Certificates

- Annexure-I: Electrical Contractor License

- Annexure-J: Power of Attorney

- Annexure-K: Blacklisting Declaration (Notarized)

- Annexure-L: General Arrangement (GA) Drawing - Preliminary

- Annexure-M: Single Line Diagram (SLD) - Preliminary

- Annexure-N: Equipment Datasheets (OEM catalogues)

# 24. Compliance Undertaking

We, Circuit Breakers India Corp., hereby undertake that the information furnished in this bid is true and correct to the best of our knowledge, and that we accept the General Terms & Conditions of Tender GSETCL/SS-MORBI/2026/EPC-021 in full, except for the deviations explicitly listed in Section 18 above. We understand that any misrepresentation discovered at any stage may result in disqualification of this bid and forfeiture of EMD/PBG, as applicable.

# 25. Evaluation Committee Remarks

This bid is rejected at the eligibility screening stage on four independent grounds (turnover shortfall, insufficient qualifying experience, restricted ISO 45001 scope, and unrectified EMD shortfall), any one of which is independently disqualifying per Section 2 of the BASE_DOC. The bidder's quoted price, while the highest among all three bids received, is recorded here for audit-trail completeness only and does not enter the L1 comparison.